Table of Contents

1.0	SCOPE	2

2.0       CODES AND STANDARDS	2

3.0       SCOPE OF SUPPLY & SERVICES	2

4.0	EXCLUSIONS	4

5.0	TERMINAL POINTS OF SUPPLY	4

6.0	LAYOUT	4

7.0       DOCUMENTS	5

7.1       Drawings/Documents Required Along With the Bid	5

7.2       Drawings/Documents To Be Submitted After Award Of Contract	5

7.3       O&M MANUAL:	5

8.0	DELIVERY (As per commercial terms and conditions)	6

9.0	Data sheet-C	6

10.0	CABLING DATA	6

11.0	SPECIFIC TECHNICAL REQUIREMENTS	6

12.0	CONSTRUCTIONAL FEATURES	19

13.0	BASE FRAMES	22

14.0	LOCAL MOTOR STARTERS	23

15.0	LOCAL PUSH BUTTON STATIONS	23

16.0	PAINTING	24

17.0     GUARANTEED PERFORMANCE REQUIREMENTS	24

18.0     QUALITY INSURANCE, INSPECTION & TESTING	25

19.0     As built drawings	26

20.0   Packing and Delivery	26

21.0	Statutory and regulatory requirements	26

22.0	CUSTOMER’S TECHNICAL SPECIFICATION	27

# 1.0	SCOPE

This specification covers the design, manufacture, assembly, testing and inspection at vendor’s/sub-vendor’s works, packing and dispatch to site of low voltage switchgear as described in the various sections of this specification.	 LV Switchgear shall generally conform to Indian Standard IS: 13947.  Erection and commissioning is not included in vendor’s scope, however the vendor shall still not be absolved of his responsibility of establishing the correctness of equipments at site.

It is not the intent to specify completely herein in all the details of the equipment. Nevertheless, the equipment shall be complete and operative in all respects and shall conform to highest standard of engineering, design and workmanship.

Specific requirements given in Data Sheet-A and Section-C of this specification shall be fully complied with.

# 2.0	CODES AND STANDARDS

The equipments and accessories covered under this specification shall be designed, manufactured and tested in accordance with latest editions of standard listed in Annexure-J to Data sheet-A and other relevant standards.

# 3.0       SCOPE OF SUPPLY & SERVICES

3.1	The scope of supply and services covers the complete supply of equipment and services in accordance with the requirements of various sections of the specification.The Scope of supply shall be as per ‘Board Wise Bill of Material’ enclosed as Annexure-B & B-1.

3.2	Purchaser reserves the right to add/delete the quantity during detailed engineering as finally required for the project.

3.3	The quantities shown in annexure are tentative for bidding purpose only and may vary up to 30% of the total order value. Any variation arising during detailed engineering stage will be taken into account for adjustment of contract price based on unit rates quoted in the bid. Bidder shall furnish unit prices of all the major items in the prescribed schedule of unit prices enclosed.

3.4	Board wise BOM (Feeder List) may vary at the time of placement of order as well as during detail engineering. Also some of the items/modules may or may not be finally ordered. Bidder shall quote unit price for each type /rating of module. The unit prices so quoted shall also be applicable for price adjustment for the changes in the module type & rating during detail engineering.

3.5	Separate base frames of ISMC-75 for switchgear erection (in addition to integral base frames) shall be supplied loose by the bidder. All fixing nuts & bolts together with foundation bolts shall also be supplied.

3.6	SPARES & CONSUMABLES

The Scope of supply shall also include the following. Bidder shall furnish item wise breakup for the Spares:

- Erection & Commissioning spares as per list enclosed.

- Recommended spares required for a period of three (3) years (OPTIONAL)

- Tools & Tackles required for operation & maintenance, as per list enclosed.

  - SCOPE OF SERVICES

- Preparation and submission of drawings & documents in soft (Both AUTOCAD & .PDF)and hard form as per the drawings / documents submission schedule.

- Submission of engineering and manufacturing status report on fortnight basis.

- Participation in project review / Technical Coordination meetings.

- Conducting performance test at shop.

- Carrying out necessary tests on electrical equipment as required by Purchaser.

- Preparation and submission of all as built drawings and O&M manual related to the contract

  - The scope of work will also include related works although they may not be specifically mentioned in the above paragraphs and all such incidental items not specified but reasonably implied and necessary for completion of the works as a whole as desired and as directed by the Purchaser / Owner.

  - The supply of required fiber optic cables, laying, and termination of cables at numerical relays up to data concentrator located in the main power house building and successful commissioning of relay communication system shall be in the scope of bidder.

  - Vendor to provide relay parameterization on IEC 61850 network. Centralized engineering PC for each unit is being provided
for Main Plant related numerical relays in Purchaser's scope.Also Vendor to consider interconnecting the relays in their scope of supply. Vendor shall provide software at Centralized engineering PC so that parameterization shall be done from Centralized engineering PC.

  - Data concentrators, Ethernet switches, Gateways,protocol convertors and required cabling till DCS required for interfacing electrical system in BTG package to DCS are in scope of Vendor only."

# 4.0	EXCLUSIONS

- Civil works

- Erection & Commissioning of switchgear

- Connection to earthing system

- Power & control cables supply and termination

# 5.0	TERMINAL POINTS OF SUPPLY

- Cable termination compartment of PCC/PMCC/MCC/DB or Terminal flange at switch board end.

- Termination at multiway terminal board for control cables.

# 6.0	LAYOUT

The bidder shall give the complete dimensions of all PCCs/MCCs/PMCCs/DBs. Any specific considerations such as minimum clearances required on all sides etc. shall be clearly brought out in the offer.

# 7.0       DOCUMENTS

## 7.1             Drawings/Documents Required Along With the Bid

Following documents are to be furnished by bidder as technical offer:

- Un-priced copyof Annexure- B, C, D, E, F, G, H, I& Price Schedule duly stamped and signed by the bidder.

- Complete dimension of all the boards including no. of panels (GA drawing not required), dimensions of each type of panels, module size of each type of feeders and minimum clearances required on all sides for each type of panels.

- A copy of the sheet “Instructions to Bidders for Preparing Technical Offer” duly stamped and signed by the bidder.

- A copy of sheet “List of Contents” duly stamped and signed by the bidder.

- Technical deviation / clarification, if any

No other information/ document (other than those mentioned above) shall be furnished by the bidder along with the technical offer, unless specificallymentioned elsewhere in specification. If so furnished, same shall not be considered by BHEL.

## 7.2		Drawings/Documents to Be Submitted After Award of Contract

No. of Drawings/documents to be submitted after award of contract shall be as per

Drawing Distribution schedule in Annexure-K.

## 7.3		O&M MANUAL:

O&M manual for installation, operation and maintenance shall be furnished         before dispatch of the equipment. Draft O&M manual shall be submitted for purchaser’s approval within two weeks of inspection. Manual shall contain minimum following details:

- Description of the equipment

- Salient construction features

- Packing details

- Instructions to be followed on receipt at site for storage

- Erection procedure & checks

- Tests to be conducted at site

- Commissioning procedure

- Maintenance instructions

- List of spares

- Approved GA drawing

- Approved Data Sheets

- Technical leaflets of all important components

7.4	For all technical tables and diagrams, calculation results, drawings, test data andScales adopted in the design the standard international unit system (SI) as per International Standardization Organization (ISO) shall be uniformly employed.

  - All engineering documents and drawings shall be of international “A” series sizes

that is of A0, A1, A2, A3 & A4.

# 8.0	DELIVERY (As per commercial terms and conditions)

# 9.0	Data sheet-C shall be duly filled up and shall be furnished after award of contract by successful bidders.

# 10.0	CABLING DATA

The power and control cable sizes shall be given separately.The power & control cable data will be used by the bidder to estimate the requirements of cable lugs and glands. Based on this data, the bidder shall resolve the constraints imposed by cabling layout inside the cable chamber/alley on panel design, module positions termination etc. For power cables, preliminary cable sizes have been indicated under Annexure-II attached.

# 11.0	SPECIFIC TECHNICAL REQUIREMENTS

11.1		The switchgear and its components shall be designed for design ambient temperature of 50º C. Project site data is indicated in Section-B. Switchgear shall be designed for natural air-cooling. No forced cooling is acceptable.

11.2	Incomers, bus-coupler and all outgoing feeders of PCCs/PMCCs/MCCs/DBs having current rating greater than 400Ashall be breaker controlled.MCC/Distribution boards up to 400A rating shall have Incomers& Bus coupler with Motorized MCCBs.

  - Motors rated from 90 KW up to and including 200 KW shall be ACB controlled and protected by comprehensive numerical motor protection relay having communication facility.

11.4	Specified Technical Parameters for equipment are covered in ‘Data Sheet-A’ enclosed.

11.5	AC distribution panels (wall mounted type) shall have MCCB units as incomer. AC distribution boards shall be of two types- one with 415V and the other with 240V outgoing feeders.

11.6	Incomers, bus couplers, outgoing feeders for each board shall be as per board wise BOM enclosed.All PCCs/PMCCs shall have at least one no. Feeder of each rating & type as spares. For breaker feeder, at least one of each type of highest rating on each bus section. All the MCCs/DBs shall have at least 20% of feeder/motor modules of each type & rating subject to one in each section. Spare modules shall be completely wired up.

Above requirement have been taken care in the BOM enclosed in Annexure-A. However, during detailed engineering stage same is to be takencare by the vendor based on the final Load Data.

11.7	Each switchboard shall have 3-phase, 3-wire system and one earth bus. All switchgear’s except DCDB’s shall be totally drawout type, floor mounted, single/double front, free standing design, single/double tier and of modular design. DCDB shall be fixed type.

  - Each switchgear shall be provided with:

- Bus PT module for each section.

- 415/240V, 1 phase panel space heating module

- 415/240V, 1 phase motor space heating module

- 415/110V Transducer power Supply module

- DC supply alarm module.

- Line VT module for each Incomer in PCC/PMCC for synchronizing purpose.

  - For each switchgear, for breaker control arrangement for receiving 2 nos. 220V DC control supply shall be provided with auto changeover to either supply. Diode changeover with RC circuit shall be provided for receiving incoming supplies. Necessary voltage monitoring contactors (for remote alarm) and indication lamp shall be provided. The 220V DC supply arrangement shall be purchaser’s responsibility.

  - PMCC/MCC shall derive 110V AC control supply through 415/110V transformer.Two 100% control supply transformers shall be provided. The auxiliary bus bars for the control power shall be segregated from the main bus bars and shall be monitored. Two selector switches shall be provided so that control power from either control transformer can be routed to control loads of other. The control transformers shall be of insulation class `B’ or better. The sizing of Control transformers shall be carried out by the Bidder considering the actual load of power contactors, auxiliary contactors, indicating lamps and other equipment including remote auxiliary relays and lamps in the circuit with 20% design margin. One pole of secondary winding shall be earthed. Each Control supply bus wires shall run throughout the board. Control supply for different modules shall be tapped individually from control supply bus. Necessary MCB/switch fuse to isolate and distribute the supply shall be provided.

  - For motor feeders rated 30 KW and above circuit for motor space heater shall be wired through NC contact of breaker/contactor.

  - All LT motors shall be controlled as follows:

a) Up to 50kW: - MPCB + Contactor (MPCB shall be with adjustable S/C

and O/L protection).

b) 50kW to 90kW shall have MCCB+ contactor+ bimetallic relay.

c) 90Kw to 160kW shall have ACB +motor protection relay (MPR).

  - The modules for the motors rated 110kW and above shall be provided with microprocessor based motor protection relays which has the cold and hotwithstand characteristics matching with motor characteristics.

  - The numerical relays shall be with communications facility 1 no. Laptop and necessary software for configuration of relay parameters shall be provided by the bidder.

11.15	CTs shall meet the requirement as per IS 2705. CTs shall be capable of carrying

120% oftheir maximum capacity continuously without exceeding the maximum

Permissible temperature rise and violating the accuracy class.

11.16	For motors rated less than 110kW, power contactors with MCCB/MPCB shall be providedin the MCCs. 110kW and above motors shall be fed by ACBs.

11.17	All breaker operated incomer and motor feeders shall be provided with 3-phase electronic energy meter suitable for interface with DDCMIS. Current transducers and ammeters shall be provided for motor feeder ≥ 30kW and for important motor feeder 30kW also.

11.18	Breaker cubicles shall be so sized as to permit closing of the front access doorwhen the breaker is pulled out to ISOLATED position. The breaker can beoperated both in service & test Position with the door closed.

11.19	The relays shall have transparent, dust tight cover, removable from front. They shallhave built in testing facilities. Except small auxiliary relays and timers, all relaysshall be drawout type. No relay shall be mounted on the rear side of PCC/PMCCpanel.

  - Current Transformers shall be cast-resin type, dry type having accuracy class 0.2S  for TVM and Incomer metering and 1.0 for others. Protective CT accuracy class shall be 5P20. All secondary connections shall be brought out to terminal blocks where wye or delta connection will be made. CT secondary shall be rated for 1A for metering and 1A for protection.

Meters shall be Digital type. All CT s/ PT s, transducers and meters (Energy accounting and audit meters) on 415 V system shall be class 1.0. Metres for

motor feeders shall be with suppressed scale.

All MCC feeders (except motor feeders) of 80kW and above rating shall have Ampere, kVA, kW transducers for communicating the data to DCS/PLC system for auxiliary consumption analysis.

All transducer shall have dual 4-20mA output and 0.5 class.

  - Voltage transformers shall be cast-resin, draw out type and shall have an accuracy class of 0.2S for TVM and Incomers metering and 1.0 for others. Voltage transformer mounted on breaker carriage is not acceptable. High voltage windings of voltage transformer shall be protected by current limiting fuses. The voltage transformer and fuses shall be completely disconnected and visibly grounded in fully draw out position.

  - All indication instruments shall be 96x96mm, 240 deg. Scale, antiglare glass and accuracy class of ± 2% full scale. Each meter shall have zero adjustment on the front.

  - Feeder list for various switchboards is enclosed in Bill of Material.

  - All the Bidirectional drives are with integral starters. Hence, necessary MCCBshall be provided for each bidirectional drives as per BOQ of applicable boards.

  - PROTECTION, CONTROL, CONTROL LOGIC AND METERING

- Communicable Numerical relays shall be provided for Protection and metering. All modules in 415V switchgear and MCC will be controlled from DCS through coupling/interposing relays. Interposing relays shall be part of switchgear/MCC. The interposing relay shall have built in LED, Test Knob & freewheeling diode.

- The relay communication system shall include the supply, installation, testing and commissioning of the following:

  - Communicable Numerical Relays

  - LAN Network along with Ethernet Switches

  - Fiber Optical cables& data Cables

  - Laptops, EWS andinterface with Numerical relays in LT Switchgear system.

  - Software for numerical relays shall be supplied and loaded in DCS. Facility for relay parameterization, maintenance, fault recording, fault analysis, trip data and trend recording and displaying shall be made available at DCS.

- Numerical Relays shall have appropriate setting ranges, accuracy, resetting ratio, transient overreach and other characteristics to provide required sensitivity.

- Numerical relays of each 415V switchboard / MCC shall be interlinked in daisy-chain arrangement or multidrop arrangement and 100% redundant output terminal shall be provided for interfaced to star coupler/Ethernet switch for upward communication.

- Relays shall have at least two output contacts for various functionality of relay. Relays shall have event recording feature, recording of abnormalities and operating parameters.

- Closing and tripping logic for breaker shall be built in Numerical Relay. Relay should have sufficient no. of Digital Inputs and Digital outputs for receiving required inputs and giving required outputs as per schematics/operational requirement. It should be able to meet all requirements as indicated in Block Logic Drawing.

- The comprehensive numerical relay shall have provision of both current and voltage inputs. The current operated relay shall have provision for 4 sets of CT inputs, 3 nos. for phase fault & 1 CT input for earth fault. The voltage-operated relay shall have provision for 3 PT inputs. Relays shall be suitable for CT secondary current of 1A/5A selectable at site.

- All CT & PT terminals shall be provided as fixed type terminals on the relay to avoid any hazard due to loose connection leading to CT opening or any other loose connection. In no circumstances Plug In type connectors shall be used for CT / PT connections. Vendor to ensure the same for all protective relay models offered.

- Relays shall have suitable output contact for breaker failure protection and shall have self diagnostic feature with self check for power failure, programmable routines, memory and main CPU failures. Relays shall have at least two sets or groups of two different sets of adaptable settings. Relays shall have multiple IEC/ ANSI programmable characteristics. Relays shall have self reset auxiliary contacts of programmable type. Design of the relay must be immune to any kind of electromagnetic interference. Vendor to submit all related type test reports for the offered model after award of contract.

- The numerical relay shall be able to provide supervisory functions such as trip circuit monitoring, measurement and recording facilities and Post fault analysis.

- All data i.e. Power, Energy, Voltage, Current and relay healthy shall be transferred to EMS/DCS through soft links.

- Schematics requiring auxiliary relays /timers for protection function shall be a part of numerical relay. The number of auxiliary relay and timer function for protection function shall be as required. Auxiliary relays for interlocking purpose shall be of self reset type. Timer functions shall be programmable for on/off delays.

- The numerical processor shall be capable of measuring and storing values of a wide range of quantities, all events, faults and disturbance recordings with a time stamping using the internal real time clock. Battery backup for real time clock in the event of power supply failure shall be provided. Necessary clock signal for time stamping shall be provided by purchaser from GPS clock installed in DDCMIS.

- 250 time tagged events /records should be able to store with time stamping. Last 5 faults storage including the indication, protection operated, operating time, currents, voltage, power energy and time.

- Diagnostics: Automatic testing, power on diagnostics with continuous monitoring to ensure high degree of reliability shall be provided. The results of the self reset functions shall be stored in battery back memory. Test features such as examination of input quantities, status of digital inputs and relay outputs shall be available on the user interface.

The alarm/status of each individual protection function and trip operation shall be communicated to DDCMIS through data concentrator (in HT switchgear scope). The numerical system shall have built-in features/hardware interface to provide such inputs to DDCMIS for analog/digital values.

- A full set of relay configuration and setting files shall be included in the design and document submission.

- Ethernet switches shall be housed in respective PCC/PMCC/MCC in separate cubicle/module with a glass window. All the relays of ACB panels shall be housed on top compartment.

- The MF (Multifunction) Meters shall have essentially Ampere, Voltage, KW, KWH and Power Factor. In addition to that if any function as on inbuilt feature then same shall be provided without any commercial implication.

- All Multifunction meters communication port for a particular board shall be wired in loop using high speed low loss data cable & shall be connected to Data concentrator through Ethernet switch. All the numerical relay communication port for a particular board shall be wired to Ethernet switch of that board with data cable. The no. of Ethernet switches for a particular board shall be decided by the bidders according to no. of relay appearing in particular board.

  - CONNECTION TO DATA CONCENTRATOR

- Ethernet switches and cables for connection of LT relays shall be in LT switchgear scope.

- FO cable required for connecting HT Ethernet switch to LT Ethernet switches, lying and termination of FO cable shall be in the scope of the vendor.

- Programming of LT Ethernet switches shall be part of vendor.

- All the data as per system architecture shall be brought up to Ethernet switch for taking it to HT switchgear DC.

- All the necessary documentation/drws/scd files/mapping details of LT relay to be provided by the LT vendor for integration. Also LT relay vendor to be deputed at site for necessary support during integration of LT relays.

- All the communicable parameters of MF meters shall be communicated through Ethernet switch to data concentrator.

- The scope of supply shall include all the material including the star coupler/Ethernet switch, Laptop PC, and interconnecting cables to it. Refer Fig.-1 attached for typical block diagram schematics for serial communication of relay with DCS.

- The protection features of numerical Relay shall be as follows:

  - Motor protection

Short circuit protection

Overload Protection

Earth fault protection

Locked rotor

Negative phase sequence

Thermal alarm

Core balance

Under voltage protection

  - Incomers/bus coupler/ outgoing breaker feeders other than motor feeder

IDMT over current protection

Three phase earth fault protection

REF Protection (for incomer from transformer only)

Under Voltage Protection (for incomer only)

  - Bus PT Feeders

Under voltage Protection

Fuse failure protection on HV and LV

- Fiber optic cable

The fiber optic cable shall be of multimode graded index OM (ISO/IEC11801) of diameter 62.5/125 Um core /gladding with max attenuation of 3.5 dB/Km at 8500nm wavelength. The cable should have rounded fiber tip with ST type connector. The cable should be suitable for operation at 850nm.

- Ethernet switches

Ethernet switches shall be ‘substation hardened’ and shall comply to IEC61850-3 for communications and environment requirements. The ethernet switches shall be  of managed type with two(2) No of fibre optic cable ports and fourteen /six of copper ports to achieve the LAN configuration indicated in the drws.These switches shall be mounted inside the switchgear panel.

- Time synchronization and GPS

Time clock synchronization equipment shall be provided and all the clocks of the numerical relays, LAN system with data concentrator, etc. shall be time synchronized. The resolution of time synchronization shall be +/- 1.0 millisecond or better throughout the entire system.

  - The successful bidder shall be fully responsible for selection and co-ordination of breaker trip and overload settings so as to provide optimum protection and discrimination of various circuits and equipment including the safety of the devices.

The bidder shall co-ordinate the overload relay with the thermal characteristics of the motor, so that these completely protect the motor. These protective devices shall not mal operate during starting of the motor.

  - ESSENTIAL SERVICE MODULE

Manual changeover/ auto changeover between the two normal incomers and their bus-coupler shall be provided. During auto changeover of the supply the contactors in the affected bus would have dropped off. The services, which shall be restarted immediately without time lapse to keep the unit running, are considered essential services. Such aux. shall restart automatically without any action by the operator after an auto changeover. These modules shall have additional hardware like timer, aux. contactors and associated circuitry in the module. Such essential services shall be identified during the detail engineering stage and suitable module/scheme shall be provided

The module of motors driving the heavy equipment like barring gear motor, air heater motor, lube oil pump, jacking oil pump, seal oil pump, scanner air fans etc., shall be provided with a CT .

  - CT primary rating for the following circuits shall be taken same as the circuit

Breaker/switch fuse/MCCB rating.

- Outgoing ACB feeders to MCC

- ACB/Motorized MCCB incomer to MCC

For other feeders to loads, the CT primary rating shall be decided on the basis of load rating/motor full load current given in the load data listing.

  - The wiring shall be complete in all aspects so as to ensure proper functioning of control protection and interlocking scheme. All the wiring shall be complete up to terminal blocks on the side of each unit / module.

Wiring shall be done with stranded copper conductor, PVC insulated,1100V gradevermin and rodent proof switchboard wire. The min. size of copper conductor used for panel wiring shall be 1.5 sq.mm for all circuits except CTs/PTs. For CTs/PTs 2.5 sq.mm wire shall be used.

  - CABLE TERMINATIONS

MCCs and DBs shall be designed to facilitate entry for external cables from bottom only. Removable gland plates of minimum thickness 3 mm shall be furnished for fitting cable glands. In case of single core cables, gland plate shall be of non-magnetic.

Sufficient space shall be provided to avoid sharp bending and for easy connectionand termination.

1100 V grade multi way terminal blocks complete with screws, nuts, washers & marking strips shall be provided by the bidder for terminating the internal wiring and outgoing cables.

Cable termination compartment and arrangement for power cables shall be suitable for heavy duty, 1.1 kV grade, stranded aluminium conductor, PVC / XLPE insulated, armoured. Heavy duty bolt-on termination tinned copper lugs of compression type shall be used in the switchgear for power cable termination. All lugs shall be insulated / sleeved. The supply of tinned copper cable lugs for power cables forms part of the supply of equipment.

Power and control terminals shall be washer head screw type or stud type complete with crimping type connectors.Screw type terminals with screws directly impinge on conductor are not acceptable. Each control terminal shall be capable for connection of 2 Nos. 2.5mm2 stranded copper wire at each end.

Double compression type cable glands of brass with conical ring for armour fixing arrangement shall be supplied loose by the bidder.

At least 20% spare terminals with a minimum of six (06) Nos. shall be provided in each module. Min. of one NO and one NC spares contacts of all contactors, relay devices shall be wired to terminal block. For CT and VT circuits disconnecting type of terminals shall be provided.

Not more than two wires will be connected to any terminal.

All control wiring shall be wired up to the terminal block at the side of the module and minimum clearance of 200mm shall be maintained between the terminal blocks and bottom plate for the lower most modules. Adjacent rows of terminal blocks shall be spaced not less than 150mm apart.

The terminal blocks shall be mounted inside the module (and not in cable way) in a manner so as to provide easy access to terminals and to enable ferrule numbers to read without difficulty.

The inter panel wiring shall be brought out to a separate set of terminal blocks near the slots meant for inter panel wires.

  - All the PCCs/PMCCs/MCCs with sectionalized buses will be normally operated with the bus coupler breakers open. Manual changeover/auto changeover between the two normal Incomers and their bus coupler will be provided with the following .

Manual changeover can be possible from one incomer to another with momentary paralleling of the two supplies. Auto changeover from one incomer to another after trip of first incomer provided it was not tripped on protection.If there is prolonged under voltage on any one of the bus sections, the respective incoming breaker shall trip and the bus coupler breaker shall close provided voltage is available on the other bus section. Total changeover time shall not exceed 1.5 seconds. This auto changeover will be blocked if the incoming breaker had tripped either on a bus fault or manually. Changeover back to the normal source of supply will be effected manually.

The automatic transfer circuit will be controlled over by an auto-manual changeover switch. The bus coupler breaker will be allowed to close only if there is no fault on affected section of the 415V switchboard bus-bars.

Manual live changeover facility will be provided for all the switchgears.When planned outage of one of the normal incoming supplies is required, the respective incomer incomers will be tripped automatically after the bus coupler is closed manually. For this purpose, a selection will be provided on the CRT in DDCMIS/PLC for selecting the incomer to be tripped.

A timer with a time delay on pick up of 0.5-5 sec. for annunciation of the running breaker failing to trip within a preset time (i.e. if the two sources remain paralleled for more than preset time) will be provided.

  - Selection of all type of relays/releases shall be subject to Customer/BHEL approval.  All relays and timers in protection circuits shall be flush mounted on panel front with connections from the inside. They shall have transparent, dust tight cover, removable from the front, a drawout construction for easy replacement and testing facility. The auxiliary relays and timers may be provided in fixed cases.  The aux. relays/timers shall not have built in batteries and shall operate on switchgear DC supply.

  - Motor starter shall be of air break, electromagnetic type as per IS: 13947 (part 4) suitable for DOL starting of motors and shall be of utilization category AC-3 for unidirectional & AC-4 for reversing starters.  Utilization category for DC contactor shall be DC-2.

  - Fuses shall be HRC, preferably link type with a minimum interrupting capacity equals to short circuit current of the LT system. Visible indication shall be provided on blowing of fuse.Fuses shall be as per IS: 13703.  Isolating switches shall have door interlocks.

  - The selection of rating of power component and the coordination with protective devices shall be done based on motor rating and characteristics. The type of co-ordination required shall be as specified in Data Sheet A in accordance with applicable standard.

  - Control and selector switches, push button and indicating lamps shall be provided as required for operation and control of switchgears / MCC and distribution boards.  Thermostatically controlled space heaters shall be furnished to keep the air inside the MCC/PCC enclosure sufficiently, above the dew point to prevent condensation.  The heaters shall be located such that wiring, buses and control devices do not get overheated.

  - The circuit breaker shall be provided with the following protective devices with suitable setting range. Shunt Trip coil for remote tripping rated for 220 V DC. It should trip at minimum 70% of rated voltage.

  - Withdrawable contactor starter units shall be provided with means for              mechanically indicating the SERVICE and other positions of trolley. The starter units shall carry designation labels in terms of module type codes, signifying the function of the unit.  Labels indicating these shall be affixed on fixed and withdrawable portion of the unit.  The units shall be designed to ensure safety of operating personnel.  Interlocks shall be provided to ensure that the unit access door can only be opened when the associated isolating device is open.

  - Bidder may, however, note that any additional auxiliary relays, auxiliary contactor, timers, etc. as required for completion of the scheme for incoming/bus coupler/outgoing circuit Breaker Panels as per the approved drawings shall not be eligible for any price adjustment.

  - Make of equipment/components for reference shall be as per list enclosed with Data sheet `A’. However, final make of equipments/components shall be subject to purchaser’s approval without any price implication.  Make of equipment/components not specified in Data sheet `A’, shall be subject to purchaser’s approval.

  - Review of the sub-contractor's documents by the contractor shall not relieve the sub - contractor from his responsibility for the design & supply.

  - Module size for each type of feeders shall be indicated. The module sizes shall be multiple of one basic unit so as to facilitate interchange ability.

  - The PCCs and MCCs shall be able to withstand the following test requirements:

• General performance requirements in accordance with IEC 60255 class 3.

• Surge withstand capability test in accordance with IEC 61000-4-5.

• Burst disturbance test in accordance with IEC 60255-22-4.

• Electrostatic discharge test in accordance with IEC 60255-22-2.

• The damp heat cyclic test in accordance with IEC 60068-2-3

• Mechanical vibration stress test in accordance with IEC 60255-21-1/2.

• The temperature ranges in service, during transport and storage in accordance with IEC 60068-2-1/2

  - The communication interface bus between Central Unit and Control modules shall be able to withstand the fast transient disturbance test in accordance with IEC 61000-4-4 class ¾. It shall also be short circuit protected.

  - Switchgear shall be subjected to all routine and acceptance tests as per relevant standards along with following tests

(a)	Temperature rise test on power circuits

(b)	Short time current tests on power circuits.

(c)	Mechanical operation test

(d)	Insulation resistance test before and after 1 minute HV test

(e)	Electrical control, interlock and sequential operation tests

(f)	Verification of wiring as per approved schematic

  - PROTECTION & CO-ORDINATION OF PROTECTION

a)	The supplier shall be responsible for providing adequate and co-ordinated scheme of protection in his equipment.  The protective devices shall be selectively co-ordinated and range and settings so selected to have a good downstream discrimination as well as quickest possible circuit isolation in case of fault.

b)	The fault on outgoing feeders from PCC/ MCCs / Distribution boards shall instantaneously cleared by the respective ACB/MCCB on the individual feeders.

c)	Opening of circuit breakers on outgoing feeders from PCC to MCC shall be time delayed so that the ACB on individual feeders as per SLD get an opportunity to clear the fault.

d)	Opening of circuit breakers controlling the main and reserve incoming supply to 415V PCC shall be sufficiently time delayed so that the breakers on outgoing feeders from these boards have the first opportunity to clear the fault.

e)	Complete protection scheme and curves demonstrating the selective co-ordination of protective element and recommended settings for protective devices shall be furnished by the successful bidder during detailed engineering stage for approval.

f)  It shall be the responsibility of the Contractor to fully coordinate the overload and short circuit tripping of the circuit breakers with the upstream and downstream circuit breakers/fuses/motor starters, to provide satisfactory discrimination.  Further the various equipments supplied shall meet the requirements of Type-II class of coordination as per IS.

g) The incomer modules shall be interlocked with their upstream breaker such that they can be closed only when upstream breaker is closed and trip automatically when upstream breaker is tripped.

h) The successfulbidder shall be fully responsible for selection and co-ordinationof breaker trip and overload settings so as to provide optimum protection anddiscrimination of various circuits and equipment including the safety of thedevices. The bidder shall co-ordinate the overload relay with the thermalcharacteristics of the motor, so that these completely protect the motor. Theseprotective devices shall not mal operate during starting of the motor.

# 12.0	CONSTRUCTIONAL FEATURES

12.1	Equipment shall be of metal enclosed, indoor, floor mounted, free standing type.  The PCCs/PMCCs/ MCCs/ distribution boards shall be fully draw out type however DBs shall be fixed type.The equipment offered shall be of proven design. Swgr shall be extensible on both sides.  Circuit breaker and feeder modules in switchboard and MCCs shall be offully draw out construction. In this type of construction it shall be possible todraw out the chassis without having to unscrew or unbolt any connections tothe equipment mounted on the withdrawable chassis. The power and control

draw out type connections shall be of sliding type. All draw out contacts,including auxiliary and control wiring shall be of self aligning type.

  - All switchboard frames, load bearing members shall be fabricated using suitable mild steel structural & sections or pressed and shaped rolled sheet steel of thickness not less than 2.5 mm.  Doors, covers & other non load bearing members shall be of cold rolled sheet steel of thickness not less than 1.6 mm.  Stiffeners shall be provided wherever necessary.  The design and construction of switchboard shall ensure adequate rigidity.

  - Where breaker/starter module front serves as compartment cover, suitable blanking covers one for each size of modules per switchboard shall be supplied for use when carriage is withdrawn.

  - The name plate shall be held by self-tapping screw. Name plate size shall be min. 20x75 mm for instruments/devices and 40x50mm for panels. Name plate for each incoming, buscoupler and outgoing at front and back on the fixed portion of the panel. For MCC warning markers shall be provided for ‘CAUTION EXTERNAL VOLTAGE’.

  - All panels shall have motor and panel space heater with independent switch/ MCB, cubicle illumination lamp with door switch.

  - Swgr height shall be 2450 mm. The working height of boards shall be limited between 250mm and 1900mm from finished floor level.It shall have vertical wire way to accommodate all cables. All the component and devices of the module shall be accessible from the front. Provision shall be provided in the switchgear for protection against accidental contact with live parts while maintaining a compartment and keeping others in service. Compartment door interlocked with main power isolating device for safety with provision for defeating it by authorized person. All cable entry should be from bottom unless otherwise specified. A horizontal separate enclosure for all auxiliary power and control bus shall be provided as required.Vertical cable alley covering entire height and min. 300mm wide and shall have hinged door. All compartments need to have covering at the bottom to preclude entry of dust, rats, lizards etc.

  - Circuit breaker shall be mounted on fully drawout truck with service, test and isolated positions and complete with following safety interlocks and safety shutters and padlock facility:Truck cannot be moved in or out of cubicle when the breaker is closed. CB compartment door shall be mechanically interlocked so that it shall not be possible to close the CB in plug position when the door is open. Insertions of breaker into service position not possible if the shutters are not free.In this type of construction it shall be possible to draw out the chassis without having to unscrew or unbolt any connections to the equipment mounted on the withdrawable chassis. The power and control draw out type connections shall be of sliding type. All draw out contacts,including auxiliary and control wiring shall be of self aligning type.

  - All busbars, bus-taps shall be insulated with close fitting sleeve of PVC insulation with high dielectric strength. All bus connectors shall be silver plated. All busbars shall be color coded (with heat shrinkable sleeves) for easy identification and so located that the sequence R-Y-B shall be from left to right, top-to bottom, or front to rear when viewed from the front of the assembly. Busbars should be adequately supported to withstand stresses developed due to short circuits. Material used for sleeving shall be capable of withstanding maximum temperatures specifiedin Data Sheet “A”. Supports shall be of glass reinforced phynolic material or cast resin. Busbar joints shall be shrouded with moulded epoxy removable shrouds.

  - Any dummy panel required for busduct entry, beam, bus coupler, cable connector, adaptors, expansion joints etc., shall be provided. Separate unit price for each type of dummy panel shall be indicated in the unit price schedule.

  - All modules of identical size & type shall be fully interchangeable without any modifications. All modules shall have service, test and withdrawn positions.

  - Switchgear shall be suitable for easy extension on both the sides. It shall be possible at a later stage at add cubicles on both sides of the switchgear by extending the busbars.

  - All cutouts shall be provided with synthetic rubber EPDM gaskets. The degree of        protection of various enclosures as per IS: 13947 shall be as follows.

a)	Compartments and busbar chambers of upto 1600 A	 IP-54

- Compartments and busbar chambers of above 1600 A with louver   IP-42

12.12	All switchboards, motor control centers (MCC) and DBs shall be divided into distinct vertical sections, each comprising of:

i)	A completely enclosed busbar compartment for running horizontal busbars.

ii) 	Individual feeder modules in multitier arrangements. Module height shall be minimum 200 mm.

iii)	Enclosed vertical busbars serving all modules in vertical section

iv)	Vertical cable alley covering entire height and minimum 300mmwide.

v)        A horizontal separate enclosure for all auxiliary power and control bus, if

required.

vi)	A compartment for relays and other control devices associated with a circuit breaker, wherever necessary.

vii)    Separate metering compartment for ACB feeders.

# 13.0	BASE FRAMES

13.1	Each switchboard shall be fitted with base frame made of angle or channel with slotted angles for field alignment with the foundation channel.All fixing nuts and bolts together with grounding bolts shall be provided.

All LT panels shall be mounted at least on 75/ 100mm integral base frame toprevent ingress of water.

Separate base frames of ISMC-75 for switchgear erection (in addition to integral base frames) shall be supplied loose by the bidder. All fixing nuts & bolts together with foundation bolts shall also be supplied.

13.2	Lifting lugs shall be provided on each shipping section. Removal of such lugs or hooks shall leave no opening in the   switchboard.

# 14.0	LOCAL MOTOR STARTERS

Local motor starters shall be metal enclosed, suitable for outdoor mounting on wall or steel structures with suitable hood on top. The enclosure shall be cold-rolled sheet steel of at least 2mm thickness. The enclosure shall be provided with a hinged guard at the front, covering full length, to avoid inadvertent operation of push buttons. The local motor starters shall be dust and vermin proof. Local motor starters (MF1 or eqvt) shall be suitable for manual switching of 415 V, 3-phase, squirrel cage motors. Local motor starter shall have a degree of protection of IP-65 with canopy& lid for outdoor &IP-54  with lid for indoor.All PBs shall be push to actuate type and stop PB shall be lockable in off position.

# 15.0	LOCAL PUSH BUTTON STATIONS

The local push buttons stations shall be metal enclosed with hood on top suitable for outdoor mounting on wall or steel structures. The enclosure shall be Poly Carbonate/ FRP/ Die-Cast Aluminium.  The enclosure shall be provided with a hinged guard at the front, covering full length, to avoid inadvertent operation of push buttons. LPBs shall have a degree of protection of IP-65 with canopy,lid for outdoor , IP-54 with lid for indoor. Terminals should be suitable for 2 cores of 2.5 Sq. Mm conductors with 20% spare terminals.

The LPBS shall have 2NO + 2NC contacts. Requirements for different type of LPBS are specified in Bill of Materials.EPB (stay put type) shall be wired directly to MCC.The EPB shall be provided with press to lock and turn to release type, keyless mechanism.

# 16.0	PAINTING

16.1 	All surfaces shall be cleaned of loose substances and foreign materials such as dirt,rust,scale, oil, grease, wielding flux etc. irrespective of whether the same has beenspelt out inthe standards or not in order that prime coat is rigidly anchored to the virgin surface.

16.2 	Surface preparation of all PCCs, PMCCs, MCCs, DBs & LPBS, Local Starters, Bus duct etc. shall be carried out in accordance with IS specification. The clean surface shall be given a phosphate coating consisting of a thin layer of zinc, iron or manganese phosphate deposited either by immersion or powder spray. The phosphate coated surface shall have one coat of baking primer of zinc chromate and two coats of stove enamel finish paint. Sufficient quantity of touch-up paint shall be furnished for application at site.

16.3 Paint shall be applied in accordance with paint manufacturer’s recommendations. The work shall generally follow IS: 1477.

16.4	All inside and outside surfaces of enclosure shall be powder coated shade no. RAL 7032.

16.5	Bidder shall furnish painting procedure during detailed engineering for purchaser’s acceptance / approval.

# 17.0       GUARANTEED PERFORMANCE REQUIREMENTS

Bidders shall guarantee that all the items/components offered by them shall meet all the requirements as stipulated in this specification & requirements as per site conditions and as confirmed by them in technical datasheets. In case, the performance of the LT Boards and components of the equipment at site is not as per the performance guarantee, the bidder shall replace the Equipment or components in them at site free of cost.

# 18.0    QUALITY INSURANCE, INSPECTION & TESTING

18.1 All materials, components and equipment’s covered under this specification shall be procured, manufactured, inspected and tested as per the BHEL/customer approved quality plan (to be submitted by vendor for approval) . There shall be no commercial implication to BHEL on account of  QP approval.

  - All equipments supplied shall be of type tested quality.

  - Successful bidder shall furnish test certificates of all type tests already carried out by the bidder on similar type of equipment after award of contract for Switchgear,Circuit Breaker, LPBsat contract stage. The type tests should have been either conducted at an independent laboratory or should have been witnessed by a reputed client. The purchaser shall review the type tests certificates furnished by the bidder at contract stage.

18.4	In absence of valid type tests certificates or in case such certificates are not found to be meeting the relevant standard requirements, vendor shall conduct all such tests according to relevant standards free of cost to purchaser and reports shall be submitted to purchaser for approval.

18.5 	Inspection shall be carried out as per the BHEL /Customer approved Quality Plan.

18.6   All important components like Switches, fuses, contactors, relays, transformers, lamps, push buttons, MCB, instruments, transducers etc shall be of type tested quality. The Contractor shall furnish type test report on components identical to those being offered for approval before fabrication of Switchgear.

18.7	All material used for the construction of the equipment shall be new and in accordance with the requirements of this specification. Materials utilized shall be those which have established themselves for use in such applications.

18.8    All tests shall be conducted as per relevant standards and shall be performed in the presence of purchaser’s representative, if so desired by the purchaser. The bidder shall give at least 21 days advance notice of the date when the tests are to be carried out.

18.9Purchaser may get type tests repeated even after submission of the valid test certificates by the bidder. Hence bidder shall indicate charges for the type test (OPTIONAL) as indicated in price schedule.

18.10Routine and type test certificates shall be furnished for all bought out items.

18.11All routine tests in accordance with the latest version of applicable standard shall be conducted for all the Switchgears. The charges for carrying out all routine tests shall be deemed to be included in the bid price.

18.12Test reports of the various tests conducted at the time of inspection shall be furnished by the vendor before dispatch of the Switchgear.

# 19.0   As built drawings

Though only supply of equipment is under bidder’s scope, bidder may note that all as-built correction (as given by purchaser to vendor) shall have to be incorporated in the originals by the vendor and copies of the as built corrected drawings/documents as per requirement shall be submitted by the vendor.

# 20.0   Packing and Delivery

The Vendor shall arrange packing as per Packing specification (ANNEXURE-P) and transportation of all Equipment from the point of manufacture to the BHEL-EPD, Bangalore. The arrangements shall include, but not be limited to, determination of routes, determination of required permits, payment of required taxes and duties, and notification to the Purchaser. Delivery (Ex-works) of all equipment shall be as per NIT. Packing drawings to be submitted for review approval. Complete closed wooden packing is only accepted. Packing quality shall be clearly specified in tender document.

# 21.0	Statutory and regulatory requirements as per IE rule 1956 with amendment-3 rule 1986, rules nos.35, 42, 50 & 51 will be adhered to.

# 22.0	LBPS

Customer’s Technical Specification for Local push Button Station,

In case of ambiguity between section-C and customer specification, vendor shall clearly brought out in technical deviation later stage it is not acceptable.

23.0	BLOCK LOGIC DIAGRAM, DRIVE CONTROL PHILISOPHY AND E-SLD have been provided as information to vendor.