Critical Points to be consider along with specification

- End Customer witness is applicable for Heat Run test for all rating of boards.

- The TVM meter shall have data storage capacity for at least 35 days in a non-volatile Memory as per CEA guidelines.

- Clarification should be given for the number of parameters that can be recorded and stored for 35 days.

- Combined Voltage and frequency variations shall be +10%.

- Busbar should be electrolytic grade as per IS 5082.

- Operating height shall be changed to 300mm, instead of 250mm given in specification.

- Undrilled gland plate to be provided.

- ISF should be indicated in drawing for CT cores envisage for TVM meters.

- Control Transformers shall be of 2 X100 % capacity with manual and auto changeover facility in case of any one Transformer supply failure

- Necessary termination to be provided to the main earth conductor (75x12 GS).

- Line PT is drawout type.

- Separate relay is not required for Line PT However the same function will uilt in existing Numerical rely of Incomer.

- TVM meter should be self powered.

- Each incomer feeder should have one no. kW, one no. kVA, three no. CTD, three no. VTD Transducer for remote metering and Each Transducer should have dual 4- 20mA outputs with 0.5 class of accuracy. .

- Metering CTs shall be provided in Bus coupler panel for local and remote metering.

- One no. kW, one no. kVA, three nos. Ammeter Transducers shall be provided in Bus coupler panel for remote metering at DCS and ECP.

- Auxiliary relay to be consider in place of Auxiliary Contactor for Control supply, Spring charging, TCS healthy, Breaker in service position and wherever continuous supply is available for auxiliary contactor. Line PT and BUS PTs supply required to be wired to remote Electrical control panel (ECP) for synchronizing purpose. Vendor to ensure that Line PT and Bus PT signals are wired upto terminal blocks in the switchgear.

- Line PT under voltage, Line PT fuse failed and Line PT not in service shall be annunciated at ECP and DDCMIS. Vendor to provide potential free contacts for this purpose.

- i) Breaker spring charged feedback shall be available at DCS.

ii) Following feedbacks shall be available at ECP also:

a) Breaker On, Off, Trip, Breaker in Remote, Breaker spring charged, Breaker Trip Ckt healthy.

iii) Incomer current (3 phases), incomer voltage (3 phases), incomer kW and incomer kVA shall be available at DCS and ECP.

iv) Incoming 220V DC control supply unhealthy shall be enunciated at DDCMIS and ECP. Vendor to provide potential free contacts for this purpose.

- "Sources paralled beyond preset time" shall be enunciated at DDCMIS and ECP. Vendor to provide potential free contacts for this purpose.

- Manual and auto changeover arrangement shall be provided for DC control supply.

- The selector switch shall have three positions namely Auto/ manual from SWGR/ Manual from SSPB.

- Vendor to ensure that Ammeter supplying for outgoing feeders should be suitable for 110V AC control supply.

- Ethernet switch shall be provided with

i)  Multimode communication

ii) Provision of Redundant bidirectional connection

iii) Four no. FO PORTS for each ethernet switch

iv) 20% spare RJ45 ports for each ethernet switch

v) Max. eight no. port is allowed for each ethernet switch