Annexure-1

Item Description: Supply and fixing of Insulating   Mat for Electrical Safety of thickness 2.5 mm as per IS: 15652 suitable for voltage up to 11 KV.

Technical Specification:

| Sr. No | Description | BHEL Requirement | Vendor Confirmation | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Composition of Insulating Mat | The insulating mats shall be made from the Material-Elastomer, free from any insertions leading to deterioration of insulating properties. |  |  |
| 2 | Thickness Of Insulating Mat | 2.5 MM ±10% |  |  |
| 3 | Tensile Strength (Min.) | 15 N/mm² |  |  |
| 4 | Elongation (Min.) | 250 % |  |  |
| 5 | Insulation resistance with water measured with 5 KV Megger (Min.) | 100000 MΩ |  |  |
| 6 | Leakage Current (Max.) | 10mA |  |  |
| 7 | Di-Electric Strength (Min.) | 45 KV |  |  |
| 8 | AC Proof Voltage | 22 KV shall withstand for 3 Minutes. (Type test certificate shall be enclosed by vendor along with technical bid) |  |  |
| 9 | Flame retardance | 5 Sec. (Type test certificate shall be enclosed by vendor along with technical bid) |  |  |
| 10 | Low temperature resistance at -10˚C ±3˚C | Shall not break or crack and also pass AC proof voltage test. (Type test certificate shall be enclosed by vendor along with technical bid) |  |  |
| 11 | Effect to Acid ,Alkali ,Diesel & Transformer oil | % change from original (Tensile & Elongation) shall not be less than 80 % and as per IS 15652. (Type test certificate shall be enclosed by vendor along with technical bid) |  |  |
| 12 | Ageing Properties at 70±1˚C for 168 Hours. | % change from original (Tensile & Elongation) shall not be less than 75 %.(Type test certificate shall be enclosed by vendor along with technical bid) |  |  |

Annexure-2

Item Description: Supply and fixing of Insulating Mat for Electrical Safety of thickness 3.0 mm as per IS: 15652 suitable for voltage 11 KV to 33 KV.

Technical Specification:

| Sr. No | Description | BHEL Requirement | Vendor Confirmation | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Composition of Insulating Mat | The insulating mats shall be made from the Material-Elastomer, free from any insertions leading to deterioration of insulating properties. |  |  |
| 2 | Thickness Of Insulating Mat | 3.0 MM ±10% |  |  |
| 3 | Tensile Strength (Min.) | 15 N/mm² |  |  |
| 4 | Elongation (Min.) | 250 % |  |  |
| 5 | Insulation resistance with water measured with 5 KV Megger (Min.) | 100000 MΩ |  |  |
| 6 | Leakage Current (Max.) | 10mA |  |  |
| 7 | Di-Electric Strength (Min.) | 65 KV |  |  |
| 8 | AC Proof Voltage | 36 KV shall withstand for 3 Minutes. (Type test certificate shall be enclosed by vendor along with technical bid) |  |  |
| 9 | Flame Retardance | 5 Sec. (Type test certificate shall be enclosed by vendor along with technical bid) |  |  |
| 10 | Low temperature resistance at -10˚C ±3˚C | Shall not break or crack and also pass AC proof voltage test. (Type test certificate shall be enclosed by vendor along with technical bid) |  |  |
| 11 | Effect to Acid ,Alkali ,Diesel & Transformer oil | % change from original (Tensile & Elongation) shall not be less than 80 % and as per IS 15652. (Type test certificate shall be enclosed by vendor along with technical bid) |  |  |
| 12 | Ageing Properties at 70±1˚C for 168 Hours. | % change from original (Tensile & Elongation) shall not be less than 75 %.(Type test certificate shall be enclosed by vendor along with technical bid) |  |  |

Annexure-3

General Terms and condition for 2.5 mm and 3.00 mm thicknesses    Insulating Mat for Electrical Safety as per IS 15652.

| Sr. No | BHEL Requirement | Vendor Confirmation | Remarks |
| --- | --- | --- | --- |
| 1 | Colour of Mat –Blue/Black |  |  |
| 2 | Anti-Skid surface design with chequered/diamond pattern without metallic derivatives |  |  |
| 3 | Length of Roll- 10 or 15 Mtr |  |  |
| 4 | Width of roll-1 Mtr |  |  |
| 5 | Marking on every roll should be as per IS 15652 i.e Class, Lot No, Roll No and Manufacturer identity. |  |  |
| 6 | Mat shall be ISI marked at every meter of length |  |  |
| 7 | Type test report as per IS 15652 for both type of Mat (2.5 MM & 3.00 mm thickness) from CPRI, ERDA or any other Government approved laboratory has to be submitted by supplier along with technical Bid. Report should not be prior to year January -2012. |  |  |
| 8 | Fixing of Mat will be in scope of supplier .Material required for fixing of Mat like adhesive, bonding agent, hardener etc. will be in scope of supplier. |  |  |
| 9 | Supplier has to quote fixing of Mat separately on running meter basis for both items individually in Rs/Meter. Fixing rate should not include rate of rubber mat .Fixing rate shall include supply of fixing material (Adhesives, bonding agent, hardener etc.) and fixing charges only. |  |  |
| 10 | Billing of fixing amount shall be done on actual measurement basis and not on the total qty of rubber mat supplied. |  |  |
| 11 | Fixing of Mat shall be done within 3 months after site clearance given by BHEL, Bhopal. |  |  |
| 12 | Pre-Dispatch inspection in accordance with IS 15652 will be carried out at manufacturer work before dispatch of material. Vendor has to intimate inspection call at least 15 in advance from date of inspection. |  |  |

Annexure-4

PQC for procurement of 2.5 mm and 3.00 mm thicknesses Insulating Mat for Electrical Safety as per IS15652.

- Only OEM of Insulating Mat for Electrical Safety or their direct authorized dealer can participate in the enquiry.

- Authorized dealer has to produce authorization certificate of OEM along with technical bid.

- Manufacturer should have at least three years’ experience in manufacturing of Insulating Mat for Electrical Safety from the date of opening of tender.

- Vendor has to submit 1 No’s of PO Copy of same items (for each sizes) supplied in last two years along with technical bid.