## Mechanical
Mechanical |  | Inter unit Scope Split :: HRRL-Barmer Captive Power Plant | [8 empty] | Rev. 00; Date : 28.11.2019
Sl. No | Item Description | Discipline | BE | DE | Supply | E&C | Sup of E&C | Civil Input | Civil Design | Civil Works | Remarks
CFBC Boiler
1 | Boiler drum, pressure parts, non pressure parts, refractory, insulation, ducting etc for CFBC | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
2 | Fuel Bunker for CFBC boiler | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
3 | Lime bunker | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
4 | Lime bunker - Feeder | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
5 | Coal conveyer system from bunker to boiler | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
6 | Bed Material bunker | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
7 | Supporting structures for coal bunker | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
8 | Goods elevator for boiler | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | If applicable
9 | Interconnecting platform between boiler and bunkers | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
10 | IBD tanks | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
11 | CBD Tanks | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
12 | HP dosing [Tri sodium Phosphate] | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
13 | PA/SA/ID fans [motor] | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
14 | Air pre heaters | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
15 | SCAPH | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
16 | Dampers and Gates | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
17 | Support structures for boiler components | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
18 | Support structures for boiler Auxiliaries | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
19 | Lifting tackles in boiler area | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
20 | Hangers and supports for IBR & Non IBR piping of Boiler Integral Piping | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
21 | Hangers and supports for Boiler integral piping | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
22 | Insulation for Boiler Integral piping | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
23 | Insulation for Integral equipment of Boiler | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
24 | Integral Valves (IBR/NIBR) of Boiler | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
25 | Integral Safety valves of Boiler | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
26 | Interconnecting gallery between coal bunkers floors for conveyor installation | Boiler & Aux. | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL
27 | Fuel oil unloading system | Boiler & Aux. | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL
28 | Fuel oil storage tank | Boiler & Aux. | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL
29 | Fuel oil forwarding pumps [motor] | Boiler & Aux. | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL
30 | HSD pressurizing Pump, scution filter and piping | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
31 | NG and Refinery Fuel Gas, srainer, control valve and piping | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
32 | LPG along with strainer, Control valve ,piping for Boiler | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
33 | FGD | Boiler & Aux. | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Interface and selection data to be furnished by Bidder along with offer.
34 | SCR | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | If applicable
35 | Electro static precipitator [ESP] | Boiler & Aux. | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Interface and selection data to be furnished by Bidder along with offer.
36 | RCC Chimney | Boiler & Aux. | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | RCC Chimeny with twin flue is applicable as per Tender.
37 | PG test and Demostration of Guarantee, PGTR etc. PG Test instruments for CFBC Boiler as required | Boiler & Aux. | Bidder | Bidder | - | - | - | - | - | -
38 | Initial fills, oils & Lubricants and required for 6 Months post Commissioning | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
39 | Equipment Foundation bolts | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
40 | 3D model and Dynamic simulation | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
41 | Alkali Boiled out/Acid Wash of Boiler | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
42 | Hydrotest of Boiler | Boiler & Aux. | Bidder | Bidder | BHEL | - | - | - | - | -
43 | Surface preparation, Painting of CFBc Boiler equipments, Piping as applicable | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
44 | Ani items required to complete the Boiler Island as per above scope matrix as per EIL specification | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
45 | Spares (O&M and Mandatory) | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
46 | Statutory Clearances (IBR etc. as required) | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
47 | Nitrogen Blanketting system | Boiler & Aux. | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder

## Electrical
Electrical |  | Scope Matrix between BHEL & CFBC Boiler bidder :: HRRL-Barmer Captive Power Plant | [8 empty] | Rev. 00; Date : 28.11.2019
Sl. No | Item Description | Discipline | BE | DE | Supply | E&C | Sup of E&C | Civil Input | Civil Design | Civil Works | Remarks
CFBC Boiler
1 | 6.6kV Switchboard | Electrical | BHEL/Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Bidder to provide the HT load list along with the location of each load to BHEL
2 | 6.6kV Cables | Electrical | BHEL/Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Bidder to provide the HT load list along with the location of each load to BHEL
3 | 6.6kV termination kits | Electrical | BHEL/Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Bidder to provide the HT load list along with the location of each load to BHEL
4 | Local control stations for HT motors pertaining to Boiler package | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
5 | Control cables between 6.6kV switchboard and LPBS of 6.6kV Motors pertaining to Boiler package | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
6 | VFDs, as applicable, for motors (HT & LT) pertaining to Boiler package | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder to provide the interface inputs like panel dimensions, heat load etc., to BHEL
7 | HT cables between Bidder's VFD and bidder's motors, if applicable | Electrical | BHEL/Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Bidder to provide the cable BOQ
8 | LT cables between Bidder's VFD and bidder's motors, if applicable | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
9 | 415V Motor Control Centers (MCCs) & DBs required for Boiler package | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder to provide the interface inputs like number of MCCs & DBs, Rating of each MCC/DB, Input power requirement (in kW) for each MCC, Heat load of MCCs, Dimensional details of each MCC etc.,
10 | Local control stations for LT motors pertaining to Boiler package | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
11 | Power & Control cables between BHEL's LT PMCC & bidder's MCCs & DBs | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder to provide the cable tray requirement for supporting these cables
12 | Downstream Power & Control cables of bidder's MCCs & DBs i.e., Bidder's MCC/DB to bidder's loads/LPBS | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder to provide the cable tray requirement for supporting these cables upto 1St coloumn of Boiler
13 | Main Lighting Distribution Board (MLDB) | Electrical | BHEL/Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Bidder to provide the feeder requirement to BHEL
14 | Cables from MLDB to bidder's lighting panles | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder to provide the cable tray requirement for supporting these cables upto 1St coloumn of Boiler
15 | UPS system & UPSDB | Electrical | BHEL/Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Bidder to provide the UPS load list to BHEL
16 | Cables from UPSDB to bidder's UPS loads | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder to provide the cable tray requirement for supporting these cables upto 1St coloumn of Boiler
17 | DC system and DCDB | Electrical | BHEL/Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Bidder to provide the HT load list along with the location of each load to BHEL
18 | Cables from DCDB to bidder's DC loads | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder to provide the cable tray requirement for supporting these cables upto 1St coloumn of Boiler
19 | DC Starter Cuibicles for bidder's DC motors | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
20 | Cable terminating accessories like glands, lugs etc., for bidder's cables on both sides | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
21 | Complete Illumination system for Boiler package including lighting panels fixtures, JBS, cables, accessories etc., | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
22 | Power receptacles, Welding receptacles with in boiler area | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
23 | Auxiliary Switchboard (ASB) for feeding receptacles | Electrical | BHEL/Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Bidder to provide the feeder requirement to BHEL
24 | Cables from ASB to bidder's Power receptacles, Welding receptacles | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder to provide the cable tray requirement for supporting these cables upto 1St coloumn of Boiler
25 | Cable trays/ducts upto 1st coloumn of each boiler (from Switchgear building) along with necessary supporting system for trays | Electrical | BHEL/Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Bidder to provide the Tray BOQ for the trays required for supporting bidder's cables upto 1 St coloumn of boiler
26 | Cable trays/ducts beyond 1st coloum of boiler (to boiler side) along with necessary supporting system for trays | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder to provide cable trays required for supporting HT cables to HT loads of boiler in addition to trays required for bidder's cables
27 | Complete Earthing system (Below Ground as well as Above Ground) for Boiler package | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | For below ground earth mat 10 mtr spacing shall be considered for tendering purpose. Exact spacing shall be decided during detail engineering stage. Same shall be complied by bidder with out any implications.
28 | Complete Lightning protection system (Below Ground as well as Above Ground) for Boiler package | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
29 | Passive Fire prrof sealing system (Mortar seal, fire break coatings) | Electrical | BHEL/Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Bidder to provide the BOQ for their cables
30 | Special Fire proof sealing system (other than Mortar seal, fire break coatings), if applicable, on boiler side | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
31 | Epoxy based Insulating coating/paint in Switchgear building for MCCs/DBs pertaining to bidder | Electrical | BHEL/Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Bidder to provide the BOQ
32 | Installation of free issued materials for Plant communication system, CCTV with in Boiler package | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
33 | Cable between Ethernet Switches in bidder's MCC & Substation Automation System (SAS) | Electrical | BHEL/Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Ethernet switches shall be considered by bidder as part of MCC
34 | Any other item required for successful operation of boiler | Electrical | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder

## C&I
Instrumentation |  | Scope Matrix between BHEL & CFBC Boiler bidder :: HRRL-Barmer Captive Power Plant | [8 empty] | Rev. 00; Date : 28.11.2019
Sl. No | Item Description | Discipline | BE | DE | Supply | E&C | Sup of E&C | Civil Input | Civil Design | Civil Works | Remarks
CFBC Boiler
1 | Distributed Control System (for monitoring instruments and simple loop) | Instrumentation | Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Bidder to submit DCS Inputs like IO count, IO list, JB grouping, cable schedule, Auto control loop/complex loop/closed loop & logics (as per BHEL format) to BHEL
2 | SIL-3 PLC (For BMS, boiler interlocks & critical Loops) System along with HMI & printer for Bolier Packge | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | BHEL | BHEL | Separate Dedicated PLC for all 4 CFBC boiler. These PLCs shall be placed in CPP control room. Bidder to furnish their civil input to BHEL.
3 | PLCs for Soot Blower for CFBC Bolier | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | BHEL | BHEL | These PLCs shall be placed in CPP control room. Bidder to furnish their civil input to BHEL.
4 | Interface of Boiler vendor's PLC with DCS | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | NA | NA | NA | Boiler supplier to coordinate with BHEL for smooth interface with DCS. Necessary support shall be extended by Bidder to boiler supplier. For DCS interface, complete terminaling accessories at PLC end shall be by Boiler supplier.
5 | Hardwired Annunciator system for Bolier(If Applicable) | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | BHEL | BHEL | Bidder to furnish civil input to BHEL
6 | HWC with PB’s/ Lamp for Boiler(If Applicable) | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | BHEL | BHEL
7 | Sequence of Event Recorder (SOE)- Standalone or Integral for Boiler along with PC and printer as per boiler specification | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | BHEL | BHEL
8 | Local Panels,Local Gauge within boiler limit | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
9 | Training, Extended warranty ,Annual Maint. Contract for PLC | Instrumentation | Bidder | Bidder | Bidder | NA | NA | NA | NA | NA
10 | SWAS (Steam and water analysis system) for CFBC Boiler | Instrumentation | Bidder | BHEL | BHEL/Bidder | BHEL/Bidder | BHEL/Bidder | BHEL | BHEL | BHEL | Bidder to furnish SWAS input including analyser count to BHEL. Bidder should take boiler area sample points (Including supply and laying of sample line) upto SWAS room.
11 | Continuous Emissions monitoring System (CEMS) for CFBC Boiler with assosciated container (prefabricated shelter) including air conditioning, power distribution, fire detection etc. as required. | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
12 | Complete Field instruments (PG, PT, PSNR, TG , LG, FE, LT, LS, DPT, DPG etc.) within boiler battery limit. | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
13 | Boiler In-line Instruments / Devices ((Temperature, flow, valve etc.) | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | NA | NA | NA
14 | Instrument mounting, hook up material for bidder supplied instruments | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | NA | NA | NA
15 | Vibration Sensors/Probes along with associated cables up to field junction box for FD Fans, SA Fans, PA Fans, ID Fans (As applicable) for CFBC Bolier | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder
16 | Vibration monitoring System (VMS) for HT drives like FD, SA, PA,ID with their HT motor drives (As applicable) | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | Bidder | BHEL | BHEL | Bidder to furnish civil input to BHEL
17 | Signal Cables & JB's - Branch Cable, Multi pair Cable, RTD Cable, T/C cable,FF cable for CFBC Boiler area upto respective control room | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | NA | NA | NA
18 | Special Cable - Fiber optic cables, serial interface cables, Network Cables etc., | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | NA | NA | NA
19 | Control room furniture for mounting of all consoles, printers, chairs for operators, operator’s desk, and file racks etc. | Instrumentation | Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL
20 | Special tools & tackles | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | NA | NA | NA
21 | Mandatory Spares, Recommended spares, O&M and maintenance spare | Instrumentation | Bidder | Bidder | Bidder | NA | NA | NA | NA | NA
22 | Cable Glands, Lugs, cable Ferrules, fasteners as required for Boiler area equipments | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | NA | NA | NA
23 | Cable Trays & accessories for C&I cables | Instrumentation | [8 empty] | Refer electical scope matrix
24 | MCT Blocks | Instrumentation | Bidder | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | BHEL | Bidder to furnish input to BHEL
25 | Training at works/ Site | Instrumentation | Bidder | Bidder | Bidder | NA | NA | NA | NA | NA
26 | Consumables and spares upto handing over to customer | Instrumentation | Bidder | Bidder | Bidder | NA | NA | NA | NA | NA
27 | Painting of Site Fabricated instruments supports, platforms and panel & equipment touch up painting etc. | Instrumentation | Bidder | Bidder | Bidder | Bidder | Bidder | NA | NA | NA