## TP
HRRL-Barmer Captive Power Plant
Terminal points between BHEL & Bidder
A) Mechanical
1. | Main steam | Upto front row of Boiler at required pressure ,temperature
2. | Feed water | From front row of Boiler at required pressure ,temperature (Feed Control station is in BHEL scope)
3. | Spray water | From Inlet of the isolating valve located ahead of spray control station
4. | Pet coke | From Inlet of crushed fuel bunker
5. | Natural Gas | From front row of Boiler at required pressure ,temperature (Feed Control station is in BHEL scope)
6. | Refiney Fuel Gas | From front row of Boiler at required pressure ,temperature (Feed Control station is in BHEL scope)
7. | LPG | From front row of Boiler at required pressure ,temperature (Feed Control station is in BHEL scope)
8. | HSD supply and return | At Suction filter of HSD pressurizing Pump near front row of Boiler
9. | Sorbent (Lime stone powder) | From Inlet of crushed limestone bunker
10 | Bed material | From Inlet of bed material bunker
11 | Bed Ash | Upto Outlet of bed ash cooler knife edge gate valve for bottom ash
12 | Fly Ash | Upto Outlet flange of hoppers below Economiser and APH for fly ash
13 | Compressed air, service air, atomizing air, instrument air | From front row of Boiler at required pressure ,temperature
14 | Cooling water | From front row of Boiler at required pressure ,temperature
15 | Drains | All high pressure drains at outlet of blow down tanks drain isolation valves. All low pressure drains are terminated at station drain / canal at ground level.
16 | Vent | At out let of CBD tank (routing to Deaerator is in BHEL scope) and all other vents to safe height in atmosphere
17 | Quenching Water for Blow down (CT Blow down water will be supplied) | From front row of Boiler at required pressure ,temperature
18 | Boiler filling | From front row of Boiler at required pressure ,temperature
19 | Nitrogen filling /purging | At front row of Boiler at required pressure ,temperature
20 | Boiler hydraulic testing | From Inlet of non-return valve in the boiler hydraulic test line.
21 | ID fan ducting | From ESP outlet. Up to Inlet of Absorber Tower of FGD
22 | Flue Gas Outlet | Upto at the inlet of ESP duct
23 | Service Water , Potable water | From At front row of Boiler at required pressure ,temperature
24 | Combustion Air | From Inlet of PA fan, SA fan and Blower, along inlet silencers and associated ductings.
B) Electrical
1. | HT Power supply: | At the consumption points of bidder's HT loads
2. | LT normal & Emergency Power supply: | (i) At the outgoing terminals of BHEL's PMCC to feed bidder's MCCs & DBs (ii) At the outgoing feeder terminals of BHEL's MLDB to feed bidder's lighting panels (iii) At the outgoing feeder terminals of BHEL's ASB to feed bidder's Welding & Power receptacles
3. | 220V DC power: | At the outgoing feeder terminals of BHEL's DCDB for feeding power to the bidder's DC loads
4. | UPS Power | At the outgoing feeder terminals of BHEL's UPSDB for feeding power to the bidder's UPS loads
5. | Earthing system:: | At two points of BHEL's below ground earth mat for interconnecting bidder's earth mat to BHEL's earth mat
6. | Lightning protection | No terminal point. Complete lightning protection is under Bidder's scope.
7. | Cable trays | At boiler 1st Coloum. Trays upto boiler 1st coloumn shall be by BHEL and beyond 1st coloumn shall be by bidder
8. | Illumination system | No terminal point. Complete lighting with in boiler package shall be by bidder.
9. | Plant communication & CCTV systems: | No terminal point. Complete Plant Communication & CCTV systems are excluded from bidder scope. However erection of the same (items free issued by BHEL) with in boiler area shall be by bidder.
C) Control & Instrumentation
1. | Instrument cable at DCS | At marshalling cabinet of DCS in CPP control room
2. | PLC interface with DCS | At PLC system cabinet
3. | SWAS | Sample points near SWAS room.
4. | Field instruments | Within Boiler battery limit