| SPECIFICATION HG/PTFE/HEP (REV 00) FOR POLY-TETRA-FLOURO-ETHYLENE LINED THRUST BEARING PADS FOR HYDROGENERATOR FOR VISHNUGAD PIPALKOTI HEP HYDROGENERATOR ENGINEERING DIVISION BHARAT HEAVY ELECTRICALS LIMITED BHOPAL – 462021 |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | PREPARED BY: | CHECKED BY: | APPROVED BY: |  |
| NAME | VG | DKC | AB |  |
| SIGN |  |  |  |  |
| DATE | 05.11.2020 | 05.11.2020 | 05.11.2020 |  |

1) TECHNICAL SPECIFICATION

1.1) INTRODUCTION:

This specification covers the scope of supply, design, performance & manufacturing requirements for Poly Tetra Fluoro Ethylene (PTFE) lined hydrodynamic thrust bearing pads for vertical Hydrogenerators.

1.2) DESCRIPTION OF PTFE LINED THRUST BEARING:

PTFE Lined thrust bearing segments is static part of Hydrogenerator, which are mounted / supported on springs in enclosed bearing housing which is filled with lubricating oil. PTFE Lined thrust bearing supports complete weight of the generator & turbine rotating parts and axial hydraulic thrust. The loading on PTFE lined thrust pads is in vertical direction and is generally in range of 100000 to 700000 kg, which varies from project to project. Continuous oil film is formed between rotating part and PTFE Lined thrust pads. PTFE shall also reduce friction losses and increase resistance to scoring as well as improve unit’s reliability. Besides very high reliability under extreme condition, the PTFE shall operate with low thermal losses and low temperatures. Operation of the PTFE lined thrust bearing pads may be unidirectional for Generator and bidirectional for generation motors.

2) SCOPE OF SUPPLY

2.1) Design of PTFE lined thrust bearing pads is in the scope of supply of Manufacturer and Latest and proven technology for bonding of the PTFE lining with the steel base should be adopted.

2.1.1) Supplier to decide the technology to be adopted for bonding of the PTFE lining with the steel pad. Metal wire or any other proven method as per latest technology, may be used for bonding of PTFE lining with base metal and shall not be projected out / upward on the edges of the pads. The bonding edges shall be smooth, with no cracks on it and shall not tear out during running of the machine.

2.1.2) Technical details of PTFE material used shall be informed by the Supplier.

2.1.3) Supplier to decide the design of the mesh to be used i.e. the supplier to decide the material of the wire, mesh density and thickness of mesh to be adopted & details shall be furnished by the Supplier.

2.1.4) Based on the bonding technology to be adopted & the mesh design, the supplier is to prepare his thrust pad manufacturing drawings.

2.1.5) The PTFE lining after bonding shall not have blow holes, cracks, uneven surface, blisters, raised face, swelling and dirt. Steel base shall not have rusting and unmachined surfaces. No crack at outer edge of PTFE. Wire mesh material shall not project at top and periphery of PTFE.

2.1.6) The radial holes for RTD and DTT shall not interfere or get punctured with each other and with HS lubrication hole.

2.1.7) The details of copper plug design for HS lubrication hole shall be furnished by the supplier as mentioned in the sample drawing.