## Unprice schedule
ANNEXURE-A
3X660 MW NORTH KARANPURA STPP
AUXILIARY SERVICE TRANSFORMERS (OIL FILLED) For ACC Application
PRICE SCHEDULE
S. No. | Item code | Item Description | Unit | Quantity | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR) | ED Nil aganinst PAC | CST/VAT @.....% of EX-Works (INR) | Service Tax @ (INR) | Freight Including Service Tax @.....% of EX-Works (INR) | Total FOR Site Price (INR)
1 | 302-11010-A | 2500kVA, 11kV/0.433kV, 3 phase, 2 winding, outdoor, ONAN, Z=13.0%, Dyn1, OFF Circuit taps ±5% in steps of 2.5% (with cable box type HV, with bus-duct type LV and with solidly grounded LVN termination) | NO. | 45
2 | 302-11000-B | OIL FILLED SERVICE TRANSFORMER - Mandatory Spares Details as per Annexure-I | SET | 1
3 | 302-11045-A | EXTRA OIL (10%) IN SEALED NON RETURNABLE STANDARD DRUMS (Type & no. of Transformers, as per annexure-II) | LOT | 1
4 | 302-11051-A | TYPE TEST (Details as per Annexure-III) | LOT | 1
Total (1.0 to 4.0)
NOTES:-
1 | BIDDER TO NOTE THAT THE COST OF TRANSFORMER SHALL INCLUDE THE COST OF ROUTINE TESTS AND SHALL BE CARRIED OUT ON ALL TRANSFORMERS WITHOUT ANY ADDITIONAL COST. BIDDER SHALL QUOTE ACCORDINGLY.
2 | BIDDER SHALL SUPPLY 10% EXTRA OIL AS PER THE QUOTED PRICE. QUANTITY OF EXTRA OIL SHALL BE SUBJECT TO APPROVAL DURING DETAIL ENGINEERING.
3 | **CHARGES FOR CARRYING OUT SHORT CIRCUIT TEST SHALL BE PAYABLE BASED ON ACTUAL INVOICE FROM DESIGNATED LABORATORIES (CPRI, BHOPAL/ CPRI, BANGLORE / ERDA, VADODARA) WITH AN ADDITIONAL LUMP SUM AMOUNT OF 5% OF EX-WORKS PRICE OF TRANSFORMER BEING TESTED TO COVER HANDLING COSTS (TRANSPORTATION, INSURANCE ETC.).
4 | IN CASE TYPE TESTS ARE WAIVED, THE TYPE TEST CHARGES SHALL NOT BE PAYABLE TO THE BIDDER
5 | CHARGES FOR ALL TYPE TESTS EXCEPT SHORT CIRCUIT TEST SHALL BE CONSIDERED FOR PRICE COMPARISONS PURPOSE.
6 | IN CASE ANY OF THE TYPE AND SPECIAL TESTS ARE REQUIRED TO BE REPEATED (IN CASE TEST FAILS OR NOT MEETING THE GUARANTEED PARAMETERS) THE SAME SHALL BE CARRIED OUT BY THE VENDOR WITHOUT ANY COMMERCIAL / DELIVERY IMPLICATION TO BHEL.

## MS
ANNEXURE-I
3X660 MW NORTH KARANPURA STPP
AUXILIARY SERVICE TRANSFORMERS (OIL FILLED) - ACC Application
PRICE SCHEDULE (MANDATORY SPARES)
S. No. | Item Description | Unit | Quantity | Unit Ex-Works (INR) Price (INR) | Total Ex-Works (INR) Price (INR) | ED Nil aganinst PAC | CST/VAT @.....% of EX-Works (INR) | Freight Including Service Tax @.....% of EX-Works (INR) | Total FOR Site Price (INR)
1 | HV bushing with metal parts & gaskets | NO EACH TYPE
a | 11.0/0.433kV, 2500KVA | NO. | 3
2 | LV bushing with metal parts & gaskets | NO EACH TYPE
a | 11.0/0.433kV, 2500KVA | NO. | 3
3 | LV Neutral bushing with metal parts & gaskets | NO EACH TYPE
a | 11.0/0.433kV, 2500KVA | NO. | 1
4 | WTI with contacts | NO EACH TYPE
a | 11.0/0.433kV, 2500KVA | NO. EACH TYPE | 1
5 | OTI with contacts | NO EACH TYPE
a | 11.0/0.433kV, 2500KVA | NO. EACH TYPE | 1
6 | Pressure relief Device | NO EACH TYPE
a | Pressure relief Device | NO. EACH TYPE | 1
7 | MOG | NO EACH TYPE
a | MOG | NO. EACH TYPE | 1
8 | Buchholz relay complete | NO EACH TYPE
a | Buchholz relay complete | NO. EACH TYPE | 1
9 | Set of gaskets | SET
a | 11.0/0.433kV, 2500KVA | SET | 1
10 | Set of valves | SET
a | 11.0/0.433kV, 2500KVA | SET | 1
11 | Air cell for conservator | NO. (AS APPLICABLE)
a | Air cell for conservator | NO. (AS APPLICABLE) | 1
Total
NOTES:-
1. 1 set consists of quantities required for 1 complete transformer of each type (as applicable).

## EXTRA OIL (10%)
ANNEXURE-II
3X660 MW NORTH KARANPURA STPP
AUXILIARY SERVICE TRANSFORMERS (OIL FILLED) - ACC Application
PRICE SCHEDULE (EXTRA OIL)
S. No. | Item Description | Unit | Quantity | Unit Ex-Works Price (INR) | Total Ex-Works Price (INR) | ED Nil aganinst PAC | CST/VAT @.....% of EX-Works (INR) | Freight Including Service Tax @.....% of EX-Works | Total FOR Site Price (INR)
EXTRA OIL (10%) IN SEALED NON RETURNABLE STANDARD DRUMS (Type & no. of Transformers, as below)
1 | 2500kVA, 11kV/0.433kV, 3 phase, 2 winding, outdoor, ONAN, Z=13.0%, Dyn1, OFF Circuit taps ±5% in steps of 2.5% (with cable box type HV, with bus-duct type LV and with solidly grounded LVN termination) | NOS. | 45
Total
NOTES:-
1. BIDDER SHALL SUPPLY 10% EXTRA OIL AS PER THE QUOTED PRICE. QUANTITY OF EXTRA OIL SHALL BE SUBJECT TO APPROVAL DURING DETAILED ENGINEERING.

## Type Test
ANNEXURE-III
3X660 MW NORTH KARANPURA STPP
AUXILIARY SERVICE TRANSFORMERS (OIL FILLED) - ACC Application
PRICE SCHEDULE (TYPE TEST)
S. No. | Description of Type Test | Unit | Quantity | Unit Prices (INR) | Total Prices (INR) | Service Tax (INR) | Total Prices Including Service Tax (INR)
1 | 2500kVA, 11kV/0.433kV, 3 phase, 2 winding, outdoor, ONAN, Z=13.0%, Dyn1, OFF Circuit taps ±5% in steps of 2.5% (with cable box type HV, with bus-duct type LV and with solidly grounded LVN termination) | NO.
1.a | TANK PRESSURE TEST | NO. | 1
1.b | TANK VACUUM TEST | NO. | 1
1.c | MEASUREMENT OF ACOUSTIC NOISE LEVEL AS PER NEMA TR-1 | NO. | 1
1.d | TEMPERATURE RISE TEST AT A TAP CORRESPONDING TO MAXIMUM LOSSES. (Gas Chromatography shall be conducted on oil sample taken before & immediately after temp. rise test. Gas analysis shall be as per IS: 9434 (based on IEC: 60567), results will be interpreted as per IS: 10593 (based on IEC: 60599). Result shall be recorded for future reference). | NO. | 1
1.e | LIGHTNING IMPULSE(FULL & CHOPPED WAVE) TEST ON WINDINGS (AS PER IEC 60076-3) | NO. | 1
1.f | SHORT CIRCUIT TEST (SPECIAL TEST) AS PER IEC 60076-5** | NO. | 1 | AS PER NOTE 1
Total
NOTES
1 | **CHARGES FOR CARRYING OUT SHORT CIRCUIT TEST SHALL BE PAYABLE BASED ON ACTUAL INVOICE FROM DESIGNATED LABORATORIES (CPRI, BHOPAL/ CPRI, BANGLORE / ERDA, VADODARA) WITH AN ADDITIONAL LUMP SUM AMOUNT OF 5% OF EX-WORKS PRICE OF TRANSFORMER BEING TESTED TO COVER HANDLING COSTS (TRANSPORTATION, INSURANCE ETC.).
2 | IN CASE TYPE TESTS ARE WAIVED, THE TYPE TEST CHARGES SHALL NOT BE PAYABLE TO THE BIDDER
3 | CHARGES FOR ALL TYPE TESTS EXCEPT SHORT CIRCUIT TEST SHALL BE CONSIDERED FOR PRICE COMPARISONS PURPOSE.
4 | IN CASE ANY OF THE TYPE AND SPECIAL TESTS ARE REQUIRED TO BE REPEATED (IN CASE TEST FAILS OR NOT MEETING THE GUARANTEED PARAMETERS) THE SAME SHALL BE CARRIED OUT BY THE VENDOR WITHOUT ANY COMMERCIAL / DELIVERY IMPLICATION TO BHEL.

## CIF
ANNEXURE-CIF
3X660 MW NORTH KARANPURA STPP, STAGE-I
AUXILIARY SERVICE TRANSFORMERS (OIL FILLED) For ACC Application
Sl. No. | Description of items to be imported. | Unit of Measurement | Qty. | Currency | Unit rate in foreign currency | Total CIF Contents
GRAND TOTAL