## ecwbending (hidden)
TALCHER STPP - 4X 500 MW
PIPE THICKNESS CLACULATIONS - ECW SYSTEM
TRANSVERSE BENDING BETWEEN SUPPORTS FOR PIPE AND FLUID WEIGHT
( ALLOWABLE STRESS : 1518 KG/CM2 FOR IS-2062 , WEIGHT DENSITY : 7850 KG/M3 )
PIPE SIZE | O.D. | THK | SPAN | I.D. | WEIGHT / M | MOMENT AT MIDDLE | MOMENT OF INERTIA | SECTION MODULUS | BENDING STRESS
( NB ) | ( MM ) | ( MM ) | MAX (M) | ( MM ) | ( KG / M ) | ( KG M ) | ( CM4 ) | ( CM3 ) | ( KG/CM2)
| D | t | L | d | W | M | I | Z | sb
200 | 219.1 | 6.4 | 5 | 206.3 | 66.9975 | 209.3672 | 2420.6687 | 220.9647 | 94.7514
250 | 273 | 6.4 | 5 | 260.2 | 95.2531 | 297.6658 | 4765.0833 | 349.0904 | 85.269
300 | 323.9 | 6.4 | 6 | 311.1 | 126.1255 | 567.5649 | 8047.2497 | 496.8972 | 114.2218
350 | 355.6 | 6 | 8 | 343.6 | 144.4548 | 1155.6386 | 10070.5528 | 566.3978 | 204.033
400 | 406.4 | 6 | 8 | 394.4 | 181.4165 | 1451.3324 | 15128.3252 | 744.5042 | 194.9394
450 | 457.2 | 6 | 8 | 445.2 | 222.4319 | 1779.4554 | 21646.8745 | 946.9324 | 187.9179
500 | 508 | 6 | 10.5 | 496 | 267.501 | 3686.4976 | 29811.534 | 1173.6824 | 314.0967
550 | 558.8 | 6 | 10.5 | 546.8 | 316.6237 | 4363.4698 | 39807.637 | 1424.7544 | 306.2612
600 | 610 | 8 | 10.5 | 594 | 395.8865 | 5455.8114 | 68551.3537 | 2247.5854 | 242.741
700 | 711.2 | 6 | 12 | 699.2 | 488.3137 | 8789.6467 | 82637.9403 | 2323.9016 | 378.228
800 | 813 | 10 | 12 | 793 | 691.9287 | 12454.7168 | 203363.9032 | 5002.802 | 248.9548
ACTUAL BENDING STRESSES AS CALCULATED ABOVE ARE MUCH LESS THAN THE ALLOWABLE BENDING STRESSES OF 1518 KG/CM2, HENCE ALL THE SELECTED PIPE THICKNESSES ARE SAFE FROM TRANSVERSE BENDING STRESSES FOR THE ABOVE CONSIDERED MAXIMUM SPANS..

## ecwsample (hidden)
| TITLE: | [7 empty] | DOCUMENT NO. PE-SC-188-165-0101
| ACW / ECW SYSTEM | [7 empty] | REV. NO. 00
| PIPE THICKNESS CALCULATIONS | [7 empty] | DATE. 02/05/2000
| 4 X 500 MW TALCHER STPP | [7 empty] | SHEET OF
A: CALCULATIONS FOR INTERNAL PRESSURE
Ref. AWWA M-11 CL. 4.1
Material |  |  | = | IS-2062 Carbon Steel encased in plane concrete
Tensile Strength ( Re ) |  |  | = | 4100 | kg/cm2
Yield Strength ( Rm ) |  |  | = | 2500 | kg/cm2
Allowable Stress ( S ) |  |  | = | 1518 | kg/cm2 (Allowable stress is lower of Re/2.7 or Rm/1.5)
Design Pressure ( P ) |  |  | = | 4 | kg/cm2 ( g )
|  |  | & | 0.1 | kg/cm2 ( a ) vacuum
| t |  | = | p x d
2 x s
| d |  | = | Outer dia. in mm
| t |  | = | Minimum specified wall thickness
| p |  | = | Pressure
| S |  | = | Allowable stress
| Pipe Nb |  | = | 2100 | mm
| OD |  | = | 2120 | mm
| t |  | = | 4 x 2120
2 x 1518
|  |  | = | 2.7931 | mm
Selected thickness |  |  | = | 14 | mm
Hence selected thickness is O.K.
B: CW SUPPLY TO CONDENSER
CALCULATION FOR EARTH LOAD AND BUOYANCY LOAD
| Pipe O.D. |  | = | 2120 | mm
|  |  | = | 6.9554 | feet
|  |  | = | 83.4646 | inch
| Radius |  | = | 41.7323 | inch
Note: | As per AWWA M11 for fabricated pipe lines buried underground,
deflection & buckling loads are the design check criteria.
B-1 : Deflection Criteria :
· Depth of Cover |  |  |  |  | = | 1.94 | M
[5 empty] | = | 6.3648 | ft.
· Pipe thickness considered |  |  |  |  | = | 14 | mm
· Pipe Material as per IS 2062
· Manufacturing tol. as per IS 2062 |  |  |  |  | = | ± | 10%
· Hence, net min. thickness available |  |  |  |  | = | 14 | - | 1.4
[5 empty] | = | 12.6
The deflection allowed in pipe line |  |  |  |  | = | 5% of pipe diameter (Refer Cl. 6.2 of AWWA M-11)
|  | Deflection Dx |  |  | = | D1 [(KWr3)/ [( EI + 0.061 E’r3)]] (As per Cl. 6.2 of AWWA M -11)
Where:
| Dx |  | = | Horizontal deflection of pipe (inch)
| D1 |  | = | Deflection lag factor (1.0 - 1.5)
| K |  | = | Bedding constant (0.1)
| W |  | = | Load/ unit of pipe length (lb/ linear inch of pipe)
| r |  | = | Radius (inch)
| EI |  | = | pipe wall stiffness (in - lb)
Where:
|  | E | = | Modulus of elasticity
|  |  | = | 30000000 |  | psi for steel
|  | I | = | Transverse moment of inertia per unit length of pipe wall
|  |  | = | t3 /12 Where ‘t’ is min. pipe thickness in inches
|  |  | = | (12.6/ 25.4)3/ 12
|  |  | = | 0.010173 |  | in3
| E’ |  | = | Modulus of soil reaction (lb/ inches2)
|  |  | = | 1000 | psi
(As per table 6.1 on page 59 of AWWA M -11)
| W |  | = | Load/ unit of pipe length
|  |  | = | Load due to soil wt. + load due to truck load
|  |  | = | (WS.HC + WT) BC
|  |  | = | (WS1.HC1 + WS2.HC2 + WT) BC
Where:
|  | WS1 | = | Unit wt. of fill (lbs/ Cu ft)
|  |  | = | 2000 | kg/M3 ( approx. )
|  |  | = | 2000 X 2.205
(3.2808)3
|  |  | = | 124.8818 | lbs/ft3
|  | WS2 | = | Unit wt. of concrete
|  |  | = | 2500 | kg/M3
|  |  | = | 2000 X 2.205
(3.2808)3
|  |  | = | 156.1023 | lbs/ft3
|  | HC1 | = | ht. Of fill above concrete on pipe approx.
|  |  | = | 1.94 | M
|  |  | = | 6.3648 | ft
|  | HC2 | = | ht. Of concrete above pipe
|  |  | = | 0 | M
|  |  | = | 0 | ft
|  | HC | = | HC1 + HC2
|  |  | = | 6.3648 | ft
|  | WT | = | Surcharge load = |  |  | 0 | psf
|  |  | = | 0 | psf as per Table 6.3 on page C-22 of AWWA M-11.
|  | BC | = | Dia of pipe
|  |  | = | 2.12 | M
|  |  | = | 6.9554 | ft
|  |  | = | 83.4646 | in
| \ W |  | = | [(125 x 5.05 + 156 x 1.64) + 2.84] x 6.96
|  |  | = | 5528.4958 |  | lbs/ ft
|  |  | = | 460.708 | lbs/ inch
| \Dx |  | = | 1.5 [ (0.1x516x 41.73 )/{(30x 106x 0.0102)+(0.061x 600x41.73)}]
|  |  | = | 1.0599 |  | in
| Dx/ D |  | = | (1.89)/(83.5 )
|  |  | = | 0.012699
|  |  | = | 1.2699 | % which is less than 5%, hence thickness selected
as 14 mm meets the deflection criteria.
B-2 : Buckling Criteria :
Allowable buckling pressure,
| qa |  | = | 1/FS (32.RW.B’.E’. EI/D3)1/2
(Refer Cl. 6.3 of AWWA - M11)
| FS |  | = | design factor
|  |  | = | 2.5 | for h/D ³ 2
|  |  | = | 3 | for h/D < 2
Where:
|  | h | = | ht. of ground surface above top of pipe (inches)
|  | D | = | dia of pipe (inches)
|  | FS | = | 6.69 / 6.96
|  |  | = | 0.91509
|  | Hence Fs | = | 3
| RW |  | = | Water bouyancy factor
|  |  | = | 1 - 0.33 (hW/h)
Where
|  | hW | = | height of water surface above top of pipe (inch)
Since in our case,
|  | hW | = | 0
| \RW |  | = | 1-0.33(hW/h)
|  |  | = | 1
| B’ |  | = | Emperical coefficient of elastic support (dimensionless)
|  |  | = | 1/ [1 + 4e ( - 0.065 H)]
Where
|  | H | = | height of fill above pipe (ft.)
| B' |  | = | 1/ [1 + 4e ( - 0.065 x 6.69)]
|  |  | = | 0.27437
| E’ |  | = | 1000 | psi
| E |  | = | 30000000 |  | psi
| qa |  | = | (1/3) [(32 x 1 x 0.28 x 600 x 30 x 106 x 0.0102)/ (83.5)3]1/2
|  |  | = | 22.6277 | psi
| Actual load |  | = | W/D
|  |  | = | 497 / 83.46
|  |  | = | 5.5198
Since allowable buckling press (qa) is higher than the actual load, hence
14mm thickness is safe in buckling.
B-3 : CHECK FOR BUCKLING UNDER COMBINED LOAD
Clause 6.3 AWWA M-11
Water load + Soil load + Vac. load £ Allowable Buckling Pressure
rw x hw x 12 + (Rw x W)/D + Pv £ qa
Where:
| rw |  | = | Specific weight of water
|  |  | = | 0.0361 |  | lb / inch3
| Pv |  | = | 0.1 | Kg/cm2 (Vacuum)
|  |  | = | 0.9 x 14.22 |  | psi
|  |  | = | 12.798 | psi
L.H.S.
|  |  | = | 0.0361 x 0.0 x 12 + (1 x 497 )/83.5 + 12.8
|  |  | = | 18.3178 | psi
R.H.S
|  |  | = | 22.6277 | psi
| \ | L.H.S. | < | R.H.S
Since allowable buckling press (qa) is higher than the combined load, hence
14mm thickness is safe.
C : CALCULATION FOR VACUUM CONDITION:
As per AWWA M-11
|  | Pc | = | 2Ex(t/D)3
(1-n2)
Where:
| Pc |  | = | Collapsing pressure (psi)
|  |  | = | 0.1 | Kg/cm2 (Vacuum)
|  |  | = | 0.9 x 14.22 |  | psi
|  |  | = | 12.798 | psi
| E |  | = | Modulus of elasticity
|  |  | = | 30000000 |  | psi for steel
| n |  | = | poisson's ratio
|  |  | = | 0.3
| t |  | = | Wall thickness (in)
| D |  | = | Pipe diameter (in)
|  |  | = | 2100 | mm
|  |  | = | 82.74 | in
using the above values in the formula, we get
| Pc |  | = | 65934065.9341 |  | x(t/D)3 psi
using a more coservative approach to account for wall thickness variation, out-of-roundness, and other
manufacturing tolerances, we get: Stewart Formula
| Pc |  | = | 50200000 |  | x(t/D)3 psi
or,
|  | t | = | (Pc / 5.02E+07)1/3xD |  |  |  | in
| \ | t | = | (12.8 / 5.02E+07)1/3 x 82.74 |  |  |  |  | in
|  |  | = | 0.52464 |  | in
|  |  | = | 13.3259 | mm
Selected thickness |  |  | = | 14 | mm
Hence selected thickness is O.K.

## WAN INDIAN
ANNEXURE - A
| PRICES SCHEDULE |  | SPECIFICATION NO. |  |  | PE-TS-408-179-N001 (Rev 0)
| PROJECT: 1X800 MW GSECL, WANAKBORI TPP, UNIT-8 |  | VOLUME |  | III
| PACKAGE :- HEAT EXCHANGERS (PLATE TYPE) |  | SECTION
| ENQUIRY No. PE/PG/WAN/E-5132/15 Dt. 18.12.2015 |  | REV. NO. |  | 00 | SHEET | 1 | OF |  | 1
[5 empty] | FOR INDIENOUS BIDDER | [6 empty] | FOR FOREIGN BIDDER
| DESCRIPTIONS OF WORKS OR EQUIPMENT |  | UNIT | QTY | UNIT Ex-works (INR) | Total Ex-works (INR) | Excise Duty @...% (for self manufactured items only) (INR) | CST @ …..% Against C-form & E1/E2 or VAT @.....% Whichever is applicable (INR) | FREIGHT (including service tax, if any ) @ …..% of total ex-works price (INR) | SERVICE TAX @ 14.5 % of PG TEST (INCLUDING SBC i.e 0.5%) (INR) | TOTAL F.O.R SITE PRICE (INR) | UNIT COST ON C & F BASIS (COST & FREIGHT BASIS - AT INDIAN PORT) (CURRENCY) | TOTAL COST ON C & F BASIS (COST & FREIGHT BASIS - AT INDIAN PORT) (CURRENCY)
SL. No. | 1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1.0 | Total price for design, manufacture, assembly, inspection and testing at manufacturer's and / or his sub contractor's works, properly packed and painted for transportation and delivery of FIVE (5) nos. PHE's (for TG & SG) complete with all accessories, commissioning spares (if any), counter flanges with nuts bolts, gaskets and coatings (wherever necessary), including special tools & tackles (if any), PG Testing, mandatory spares etc., as specified in bidder's scope of supply as per Technical Specification PE-TS-408-179-N001 including all taxes & duties. |  | 2: SETS; 3: 5
2.0 | Break-Up of Prices at sl no 1.0
2.1 | a)PHE for TG Auxiliaries. |  | 2: Nos.; 3: 3
| b)PHE for SG Auxiliaries. |  | 2: Nos.; 3: 2
2.2 | Mandatory spares (DETAILS AS PER Annexure -1A) |  | 2: Set; 3: 1
2.3 | Lump sum price for E&C Spares |  | 2: Set; 3: 1
2.4 | Lump sum price for Tools and Tackles (if required) |  | 2: Set; 3: 1
2.5 | Lumpsum Price for Site Performance Testing of all PHE's (PG TEST) |  | 2: Set; 3: 1
3.0 | GRAND TOTAL FOR EVALUATION (2.1 + 2.2+2.3+2.4 +2.5)
4.0 | CIF CONTENT (indicating the list of items,QTY, currency, rate of custom duty along with the source of supply) considered in your prices. (Please attach separate sheet for details of items with their break-up of prices- Refer Annex - B).
OPTIONAL PRICES
5.0 | RECOMMENDED SPARES
RECOMMENDED SPARES :- Item-wise break up with item-wise price to be given as per “Schedule of Recommended Spares” enclosed under Vol. III of technical specification. Recommended spares are only for reference purpose and not to be considered for evaluation and ordering purpose
Note :
a) | The values indicated at 1.0 & 3.0 should match. In case of any descrepancy, the evaluation shall be done as per cl no 11.0 of GCC Rev-05 (Instructions to bidders).
b) | Unit prices quoted by the bidder, as above, shall be binding for any quantity variation which is at discretion of Purchaser.
c) | Indicate all duties, taxes etc. Stating whether included/ excluded in above price.
d) | Price of commissioning & erection spares and other accessories not listed above shall be included in the price of equipment & shall be supplied with the equipment
e) | Price break up for items not asked are deemed to be included 1.0.
Your prices should be as per this 'Format' only.
PARTICULARS OF BIDDER/ AUTHORISED REPRESENTATIVE
NAME |  | DESIGNATION | 2: SIGNATURE; 5: DATE; 7: COMPANY SEAL

## MANDATORY
ANNEXURE - I A
|  |  |  | PROJECT | :- 1X800 MW GSECL, WANAKBORI TPP, UNIT-8
|  |  |  | PACKAGE | :- HEAT EXCHANGERS (PLATE TYPE)
|  |  |  | ENQUIRY No. | :- PE/PG/WAN/E-5132/2015 Dtd. 18.12.2015
[7 empty] | FOR INDIENOUS BIDDER (INR) | [5 empty] | FOR FOREIGN BIDDER
| DESCRIPTIONS OF WORKS OR EQUIPMENT (AS PER DATA SHEET - A OF TECHNICAL SPECIFICATION NO PE-TS-408-179-N001 (Rev 0) |  |  |  | QTY | Unit | UNIT Ex-works (INR) | Total Ex-works (INR) | Excise Duty @...% (for self manufactured items only) (INR) | CST @ …..% Against C-form & E1/E2 or VAT @.....% Whichever is applicable (INR) | FREIGHT (including service tax, if any ) @ …..% of total ex-works price (INR) | TOTAL F.O.R. SITE PRICE | UNIT COST ON C & F BASIS (COST & FREIGHT BASIS - AT INDIAN PORT) (CURRENCY) | TOTAL COST ON C & F BASIS (COST & FREIGHT BASIS - AT INDIAN PORT) (CURRENCY)
I | HEAT EXCHANGERS |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | MANDATORY SPARES
| a) |  |  | PLATES | 1: 5% for each Category of material, size and thickness
| b) | b) | b) | valves | 1: 10% or Minimum 1 No. For each type, size and Pressure rating Whichever is higher
2 | GRAND TOTAL

## CIF
ANNEXURE -B
PROJECT | :- 1X800 MW GSECL, WANAKBORI TPP, UNIT-8
PACKAGE | :- HEAT EXCHANGERS (PLATE TYPE)
ENQUIRY No. | :- PE/PG/WAN/E-5132/2015 Dtd. 18.12.2015
| Discription | UNIT | QUANTITY | CURRENCY | RATE OF CUSTOM DUTY | SOURCE OF SUPPLY | TOTAL CIF CONTENT
LIST OF CIF CONTENTS FOR HEAT EXCHANGERS (PLATE TYPE) FOR 1X800 MW GSECL, WANAKBORI TPP, UNIT-8
SL NO. | 1 | 2 | 3 | 4 | 5 | 6 | 7
1
2
3
4
5
6
7
8
9
10
11
12
13
14
Bidder shall furnish this price schedule in his price offer only
Particulars of bidder / authorised representative
Name | Designation |  |  |  | Signature | Date | Company seal