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	QUANTUM OF CHECK
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	Item : THERMOWELL 

	
	
	
	
	
	
	
	
	
	
	
	

	1.0
	RAW MATERIALS & BOUGHT OUT ITEMS

	1.1
	BAR, etc.
	CHEMICAL COMPOSITION
	MAJOR
	MATERIAL TEST
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	MATERIAL TEST CERTIFICATE
	√
	2
	--
	1
	

	2.0
	FINAL INSPECTION & TESTING

	2.1
	THERMOWELL
	PHYSICAL VERIFICATION & MARKING CHECK
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	2.2
	
	DIMENSIONAL VERIFICATION
	MAJOR
	MEASUREMENT
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	DIMENSION REPORT
	√
	2
	1
	--
	10% WITNESS BY “1”

	2.3
	
	PRESSURE TEST
	MAJOR
	LEAKAGE
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	1
	--
	10% WITNESS BY “1”

	2.4
	
	GUARANTEE PERFORMANCE
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	GUARANTEE CERTIFICATE
	√
	2
	--
	1
	

	3.0
	PRESERVATION & PACKING

	3.1
	COMPLETE ASSEMBLY
	PACKING & PRESERVATION
	MAJOR
	PACKING
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	PACKING LIST
	√
	2
	--
	1
	


NOTE:-

1. This standard MQP should be read along with specification (latest revision), approved drawings & approved data sheet.

2. Drawing/data sheet shall prevail over quality plan for contradiction if any between quality plan and drawing/specification.

3. All test certificates/reports reviewed and certified by TPI/BHEL shall be submitted to BHEL as documentation package.

4. All type test reports submitted shall not be older than 5 yrs from the date of purchase order.

5. Any project/customer specific requirements which shall be notified have to be fulfilled by the vendor at the time of execution of order.

	 Item : PRESSURE TRANSMITTER 

	
	
	
	
	
	
	
	
	
	
	
	

	1.0
	RAW MATERIALS & BOUGHT OUT ITEMS

	1.1
	PRESSURE TRANSMITTER
	MATERIAL OF CONSTRUCTION
	MAJOR
	MATERIAL CONFIRMITY
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	MATERIAL COMPLIANCE CERTIFICATE
	√
	2
	--
	1
	

	2.0
	FINAL INSPECTION & TESTING

	2.1
	PRESSURE TRANSMITTER
	PHYSICAL VERIFICATION & MARKING CHECK
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	2.2
	
	CALIBRATION
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	CALIBRATION TEST CERTIFICATE
	√
	2
	--
	1
	

	2.3
	
	EXPLOSION PROOF 
	MAJOR
	VERIFICATION
	FOR ONE SAMPLE OF PARTICULAR DESIGN 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	EXPLOSION PROOF CERTIFICATE (
	√
	2
	--
	1
	

	2.4
	
	INTRINSIC SAFE
	MAJOR
	VERIFICATION
	FOR ONE SAMPLE OF PARTICULAR DESIGN 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	CERTIFICATE FOR INTRINSIC SAFE EXECUTION
	√
	2
	--
	1
	

	2.5
	
	GUARANTEE PERFORMANCE
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	GUARANTEE CERTIFICATE
	√
	2
	--
	1
	

	3.0
	PRESERVATION & PACKING

	3.1
	COMPLETE ASSEMBLY
	PACKING & PRESERVATION
	MAJOR
	PACKING
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	PACKING LIST
	√
	2
	--
	1
	


NOTE:-

1. This standard MQP should be read along with specification (latest revision), approved drawings & approved data sheet.

2. Drawing/data sheet shall prevail over quality plan for contradiction if any between quality plan and drawing/specification.

3. All test certificates/reports reviewed and certified by TPI/BHEL shall be submitted to BHEL as documentation package.

4. All type test reports submitted shall not be older than 5 yrs from the date of purchase order.

5. Any project/customer specific requirements which shall be notified have to be fulfilled by the vendor at the time of execution of order.

	Item : DIFFERENTIAL PRESSURE TRANSMITTER (REMOTE SEAL DPT) 

	
	
	
	
	
	
	
	
	
	
	
	

	1.0
	RAW MATERIALS & BOUGHT OUT ITEMS

	1.1
	DIFFERENTIAL PRESSURE TRANSMITTER
	MATERIAL OF CONSTRUCTION
	MAJOR
	MATERIAL CONFIRMITY
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	MATERIAL TEST CERTIFICATE
	√
	2
	--
	1
	

	2.0
	FINAL INSPECTION & TESTING

	2.1
	DIFFERENTIAL PRESSURE TRANSMITTER
	PHYSICAL VERIFICATION & MARKING CHECK
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	2.2
	
	FIVE POINT CALIBRATION
	MAJOR
	REVIEW
	10% or min. 2 nos. randomly
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	CALIBRATION TEST CERTIFICATE
	√
	2
	1
	--
	

	2.3
	
	HYDRO TEST FOR PRESSURE PARTS
	MAJOR
	LEAKAGE
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	--
	1
	

	2.4
	
	FUNCTIONAL TEST (OUTPUT, HART, ACCURACY, DIAGNOSIS, DISPLAY)
	MAJOR
	PERFORMANCE
	10% or min. 2 nos. randomly
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	1
	--
	

	2.5
	
	BILL OF MATERIAL (MODEL, DIMENSIONS, TAG NO.) 
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	2.6
	
	SPARES* (BOM, PART NOS)
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	* if ordered

	2.7
	
	EXPLOSION PROOF 
	MAJOR
	VERIFICATION
	FOR ONE SAMPLE OF APPLICABLE DESIGN 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	EXPLOSION PROOF CERTIFICATE
	√
	2
	--
	1
	

	2.8
	
	INTRINSIC SAFE
	MAJOR
	VERIFICATION
	FOR ONE SAMPLE OF APPLICABLE DESIGN 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	CERTIFICATE FOR INTRINSIC SAFE EXECUTION
	√
	2
	--
	1
	

	2.9
	
	WEATHER PROOFNESS
	MAJOR
	VERIFICATION
	FOR ONE SAMPLE OF APPLICABLE DESIGN 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	IP CERTIFICATE
	√
	2
	--
	1
	

	3.0
	PRESERVATION & PACKING

	3.1
	COMPLETE ASSEMBLY
	PACKING & PRESERVATION
	MAJOR
	PACKING
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	PACKING LIST
	√
	2
	--
	1
	


NOTE:-

1. This MQP should be read along with specification (latest revision), approved drawings & approved data sheet.

2. Drawing/data sheet shall prevail over quality plan for contradiction if any between quality plan and drawing/specification.

3. All test certificates/reports reviewed and certified by TPI/BHEL shall be submitted to BHEL as documentation package.

4. All type test reports submitted shall not be older than 5 yrs from the date of purchase order.

5. Any project/customer specific requirements which shall be notified have to be fulfilled by the vendor at the time of execution of order.

	Item : DIFFERENTIAL PRESSURE TRANSMITTER

	
	
	
	
	
	
	
	
	
	
	
	

	1.0
	RAW MATERIALS & BOUGHT OUT ITEMS

	1.1
	DIFFERENTIAL PRESSURE TRANSMITTER
	MATERIAL OF CONSTRUCTION
	MAJOR
	MATERIAL CONFIRMITY
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	MATERIAL COMPLIANCE CERTIFICATE
	√
	2
	--
	1
	

	2.0
	FINAL INSPECTION & TESTING

	2.1
	DIFFERENTIAL PRESSURE TRANSMITTER
	PHYSICAL VERIFICATION & MARKING CHECK
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	2.2
	
	CALIBRATION
	MAJOR
	REVIEW
	10% or min. 2 nos. randomly
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	CALIBRATION TEST CERTIFICATE
	√
	2
	1
	--
	

	2.3
	
	EXPLOSION PROOF 
	MAJOR
	VERIFICATION
	FOR ONE SAMPLE OF APPLICABLE DESIGN 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	EXPLOSION PROOF CERTIFICATE
	√
	2
	--
	1
	

	2.4
	
	INTRINSIC SAFE
	MAJOR
	VERIFICATION
	FOR ONE SAMPLE OF APPLICABLE DESIGN 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	CERTIFICATE FOR INTRINSIC SAFE EXECUTION
	√
	2
	--
	1
	

	2.5
	
	GUARANTEE PERFORMANCE
	MAJOR
	VERIFICATION
	FOR ONE SAMPLE OF APPLICABLE DESIGN 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	GUARANTEE CERTIFICATE
	√
	2
	--
	1
	

	3.0
	PRESERVATION & PACKING

	3.1
	COMPLETE ASSEMBLY
	PACKING & PRESERVATION
	MAJOR
	PACKING
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	PACKING LIST
	√
	2
	--
	1
	


NOTE:-

1. This standard MQP should be read along with specification (latest revision), approved drawings & approved data sheet.

2. Drawing/data sheet shall prevail over quality plan for contradiction if any between quality plan and drawing/specification.

3. All test certificates/reports reviewed and certified by TPI/BHEL shall be submitted to BHEL as documentation package.

4. All type test reports submitted shall not be older than 5 yrs from the date of purchase order.

5. Any project/customer specific requirements which shall be notified have to be fulfilled by the vendor at the time of execution of order.

	Item : THERMOCOUPLE TEMPERATURE DETECTOR 

	
	
	
	
	
	
	
	
	
	
	
	

	1.0
	RAW MATERIALS & BOUGHT OUT ITEMS

	1.1
	THERMO ELEMENT, etc.
	CHEMICAL & PHYSICAL PROPERTIES
	MAJOR
	COMPOSITION
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	MATERIAL TEST CERTIFICATE
	√
	2
	--
	1
	

	2.0
	FINAL INSPECTION & TESTING

	1.1. 
	THERMOCOUPLE
	PHYSICAL VERIFICAITON & MARKING CHECK
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	1.2. 
	
	CALIBRATION
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	CALIBRATION GUARANTEE CERTIFICATE
	√
	2
	--
	1
	

	1.3. 
	
	DIMENSION VERIFICATION
	MAJOR
	MEASUREMENT
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	10% WITNESS BY “1”

	1.4. 
	THERMOCOUPLE – ROUTINE TESTS
	ACCURACY TEST
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	1.5. 
	
	INSULATION RESISTANCE TEST AT 27 ± 20 C AND RELATIVE HUMIDITY OF 45 TO 75 %
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	1.6. 
	
	DIMENSIONAL CHECKUP
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	1.7. 
	THERMOCOUPLE – TYPE TESTS
	ACCURACY TEST
	MAJOR
	REVIEW
	ON ONE SAMPLE OF APPLICABLE DESIGN/ MODEL 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	1.8. 
	
	INSULATION RESISTANCE TEST AT 6000 C
	MAJOR
	REVIEW
	ON ONE SAMPLE OF APPLICABLE DESIGN/ MODEL 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	1.9. 
	
	RESPONSE TIME (THERMAL LAG) TEST
	MAJOR
	REVIEW
	ON ONE SAMPLE OF APPLICABLE DESIGN/ MODEL 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	1.10. 
	
	VIBRATION TEST
	MAJOR
	REVIEW
	ON ONE SAMPLE OF APPLICABLE DESIGN/ MODEL 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	1.11. 
	
	GUARANTEE PERFORMANCE
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	GUARANTEE CERTIFICATE
	√
	2
	--
	1
	

	3.0
	PRESERVATION & PACKING

	3.1
	COMPLETE ASSEMBLY
	PACKING & PRESERVATION
	MAJOR
	PACKING
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	PACKING LIST
	√
	2
	--
	1
	


NOTE:-

1. This standard MQP should be read along with specification (latest revision), approved drawings & approved data sheet.

2. Drawing/data sheet shall prevail over quality plan for contradiction if any between quality plan and drawing/specification.

3. All test certificates/reports reviewed and certified by TPI/BHEL shall be submitted to BHEL as documentation package.

4. All type test reports submitted shall not be older than 5 yrs from the date of purchase order.

5. Any project/customer specific requirements which shall be notified have to be fulfilled by the vendor at the time of execution of order.

	Item : PRESSURE GAUGE 

	
	
	
	
	
	
	
	
	
	
	
	

	1.0
	RAW MATERIALS & BOUGHT OUT ITEMS

	1.1
	PRESSURE GAUGE
	MATERIAL OF CONSTRUCTION
	MAJOR
	MATERIAL CONFIRMITY
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	MATERIAL COMPLIANCE CERTIFICATE
	√
	2
	--
	1
	

	2.0
	FINAL INSPECTION & TESTING

	2.1
	PRESSURE GAUGE
	VISUAL & MARKING CHECK
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	2.2
	
	CALIBRATION
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	CALIBRATION TEST CERTIFICATE
	√
	2
	--
	1
	

	2.3
	
	WEATHER- PROOFNESS
	MAJOR
	TYPE TEST
	ON ONE SAMPLE OF APPLICABLE DESIGN/ MODEL 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	IP CERTIFICATE
	√
	2
	--
	1
	

	2.4
	
	GUARANTEE PERFORMANCE
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	GUARANTEE CERTIFICATE
	√
	2
	--
	1
	

	3.0
	PRESERVATION & PACKING

	3.1
	COMPLETE ASSEMBLY
	PACKING & PRESERVATION
	MAJOR
	PACKING
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	PACKING LIST
	√
	2
	--
	1
	


NOTE:-

1. This standard MQP should be read along with specification (latest revision), approved drawings & approved data sheet.

2. Drawing/data sheet shall prevail over quality plan for contradiction if any between quality plan and drawing/specification.

3. All test certificates/reports reviewed and certified by TPI/BHEL shall be submitted to BHEL as documentation package.

4. All type test reports submitted shall not be older than 5 yrs from the date of purchase order.

5. Any project/customer specific requirements which shall be notified have to be fulfilled by the vendor at the time of execution of order.

	Item : DIFFERENTIAL PRESSURE GAUGE 

	
	
	
	
	
	
	
	
	
	
	
	

	1.0
	RAW MATERIALS & BOUGHT OUT ITEMS

	1.1
	DIFFERENTIAL PRESSURE GAUGE –SENSOR & CASE OF INSTRUMENT etc.
	MATERIAL OF CONSTRUCTION
	MAJOR
	MATERIAL CONFIRMITY
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	MATERIAL COMPLIANCE CERTIFICATE
	√
	2
	--
	1
	

	2.0
	FINAL INSPECTION & TESTING

	2.1
	DIFFERENTIAL PRESSURE GAUGE
	PHYSICAL VERIFICATION & MARKING CHECK
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	2.2
	
	CALIBRATION
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	CALIBRATION TEST CERTIFICATE
	√
	2
	--
	1
	

	2.3
	
	WEATHER PROOF
	MAJOR
	TYPE TEST
	ON ONE SAMPLE OF APPLICABLE DESIGN/ MODEL 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	IP CERTIFICATE
	√
	2
	--
	1
	

	2.4
	
	ACCURACY TEST
	MAJOR
	TYPE TEST
	ON ONE SAMPLE OF APPLICABLE DESIGN/ MODEL 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	2.5
	
	MAXIMUM WORKING PRESSURE WITHSTAND ABILITY
	MAJOR
	TYPE TEST
	ON ONE SAMPLE OF APPLICABLE DESIGN/ MODEL 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	2.6
	
	GUARANTEE PERFORMANCE
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	GUARANTEE CERTIFICATE
	√
	2
	--
	1
	

	3.0
	PRESERVATION & PACKING

	3.1
	COMPLETE ASSEMBLY
	PACKING & PRESERVATION
	MAJOR
	PACKING
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	PACKING LIST
	√
	2
	--
	1
	


NOTE:-

1. This standard MQP should be read along with specification (latest revision), approved drawings & approved data sheet.

2. Drawing/data sheet shall prevail over quality plan for contradiction if any between quality plan and drawing/specification.

3. All test certificates/reports reviewed and certified by TPI/BHEL shall be submitted to BHEL as documentation package.

4. All type test reports submitted shall not be older than 5 yrs from the date of purchase order.

5. Any project/customer specific requirements which shall be notified have to be fulfilled by the vendor at the time of execution of order.
	Item : TEMPERATURE GAUGE 

	
	
	
	
	
	
	
	
	
	
	
	

	1.0
	RAW MATERIALS & BOUGHT OUT ITEMS

	1.1
	BOURDON,TUBE,MOVEMENT,BULB,STEM  & PROCESS CONNECTION GLAND, etc.
	MATERIAL OF CONSTRUCTION
	MAJOR
	MATERIAL CONFIRMITY
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	MATERIAL COMPLIANCE CERTIFICATE
	√
	2
	--
	1
	

	2.0
	FINAL INSPECTION & TESTING

	2.1
	TEMPERATURE GAUGE
	PHYSICAL VERIFICATION & MARKING CHECK
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	2.2
	
	CALIBRATION
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	CALIBRATION TEST CERTIFICATE
	√
	2
	--
	1
	

	2.3
	TEMPERATURE GAUGE – ROUTINE TEST
	ACCURACY TEST
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	2.4
	TEMPERATURE GAUGE – TYPE TESTS
	OVER -TEMPERATURE STABILITY TEST
	MAJOR
	REVIEW
	ON ONE SAMPLE OF APPLICABLE DESIGN/ MODEL 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	2.5
	
	ACCURACY TEST
	MAJOR
	REVIEW
	ON ONE SAMPLE OF APPLICABLE DESIGN/ MODEL 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	2.6
	
	RESPONSE TIME TEST
	MAJOR
	REVIEW
	ON ONE SAMPLE OF APPLICABLE DESIGN/ MODEL 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	2.7
	
	DUST & WATER TIGHT TEST
	MAJOR
	REVIEW
	ON ONE SAMPLE OF APPLICABLE DESIGN/ MODEL 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	IP CERTIFICATE
	√
	2
	--
	1
	

	2.8
	TEMPERATURE GAUGE


	GUARANTEE PERFORMANCE
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	GUARANTEE CERTIFICATE
	√
	2
	--
	1
	

	3.0
	PRESERVATION & PACKING

	3.1
	COMPLETE ASSEMBLY
	PACKING & PRESERVATION
	MAJOR
	PACKING
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	PACKING LIST
	√
	2
	--
	1
	


NOTE:-

1. This standard MQP should be read along with specification (latest revision), approved drawings & approved data sheet.

2. Drawing/data sheet shall prevail over quality plan for contradiction if any between quality plan and drawing/specification.

3. All test certificates/reports reviewed and certified by TPI/BHEL shall be submitted to BHEL as documentation package.

4. All type test reports submitted shall not be older than 5 yrs from the date of purchase order.

5. Any project/customer specific requirements which shall be notified have to be fulfilled by the vendor at the time of execution of order.

	Item : LEVEL GAUGE 

	
	
	
	
	
	
	
	
	
	
	
	

	1.0
	RAW MATERIALS & BOUGHT OUT ITEMS

	1.1
	LEVEL GAUGE
	MATERIAL OF CONSTRUCTION
	MAJOR
	MATERIAL CONFIRMITY
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	MATERIAL COMPLIANCE CERTIFICATE
	√
	2
	--
	1
	

	2.0
	FINAL INSPECTION & TESTING

	2.1
	LEVEL GAUGE
	PHYSICAL VERIFICATION & MARKING CHECK
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	2.2
	
	COROSSION TEST
	MAJOR
	TEST
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	2.3
	
	THERMAL SHOCK TEST
	MAJOR
	TEST
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	2.4
	
	HYDRAULIC TEST
	MAJOR
	TEST
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	TEST CERTIFICATE
	√
	2
	--
	1
	

	2.5
	
	IBR CERTIFICATE*
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	IBR FORM - III C
	√
	2
	--
	1
	*if applicable

	2.6
	
	GUARANTEE PERFORMANCE
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	GUARANTEE CERTIFICATE
	√
	2
	--
	1
	

	3.0
	PRESERVATION & PACKING

	3.1
	COMPLETE ASSEMBLY
	PACKING & PRESERVATION
	MAJOR
	PACKING
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	PACKING LIST
	√
	2
	--
	1
	


NOTE:-

1. This standard MQP should be read along with specification (latest revision), approved drawings & approved data sheet.

2. Drawing/data sheet shall prevail over quality plan for contradiction if any between quality plan and drawing/specification.

3. All test certificates/reports reviewed and certified by TPI/BHEL shall be submitted to BHEL as documentation package.

4. All type test reports submitted shall not be older than 5 yrs from the date of purchase order.

5. Any project/customer specific requirements which shall be notified have to be fulfilled by the vendor at the time of execution of order.

	MAGNETIC FLOW METER

	
	
	
	
	
	
	
	
	
	
	
	

	1.0
	RAW MATERIALS & BOUGHT OUT ITEMS

	1.1
	MAGNETIC FLOW METER
	MATERIAL OF CONSTRUCTION
	MAJOR
	MATERIAL CONFIRMITY
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	MATERIAL COMPLIANCE CERTIFICATE
	√
	2
	--
	1
	

	2.0
	FINAL INSPECTION & TESTING

	2.1
	MAGNETIC FLOW METER
	PHYSICAL VERIFICATION & MARKING CHECK
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	2.2
	
	CALIBRATION
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	CALIBRATION TEST CERTIFICATE
	√
	2
	--
	1
	

	3.0
	PRESERVATION & PACKING

	3.1
	COMPLETE ASSEMBLY
	PACKING & PRESERVATION
	MAJOR
	PACKING
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	PACKING LIST
	√
	2
	--
	1
	


NOTE:-

1. This standard MQP should be read along with specification (latest revision), approved drawings & approved data sheet.

2. Drawing/data sheet shall prevail over quality plan for contradiction if any between quality plan and drawing/specification.

3. All test certificates/reports reviewed and certified by TPI/BHEL shall be submitted to BHEL as documentation package.

4. All type test reports submitted shall not be older than 5 yrs from the date of purchase order.

5. Any project/customer specific requirements which shall be notified have to be fulfilled by the vendor at the time of execution of order.

	Item : JUNCTION BOX 

	
	
	
	
	
	
	
	
	
	
	
	

	1.0
	RAW MATERIALS & BOUGHT OUT ITEMS

	1.1
	JUNCTION BOX
	MATERIAL OF CONSTRUCTION
	MAJOR
	MATERIAL TEST
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	MATERIAL TEST CERTIFICATE
	√
	2
	--
	1
	

	2.0
	FINAL INSPECTION & TESTING

	2.1
	JUNCTION BOX
	PHYSICAL VERIFICATION
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	2.2
	
	NAME PLATE MARKING VERIFICATION
	MAJOR
	VERIFY
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	2.3
	
	WEATHER PROOFNESS
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	IP CERTIFICATE
	√
	2
	--
	1
	

	3.0
	PRESERVATION & PACKING

	3.1
	COMPLETE ASSEMBLY
	PACKING & PRESERVATION
	MAJOR
	PACKING
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	PACKING LIST
	√
	2
	--
	1
	


NOTE:-

1. This standard MQP should be read along with specification (latest revision), approved drawings & approved data sheet.

2. Drawing/data sheet shall prevail over quality plan for contradiction if any between quality plan and drawing/specification.

3. All test certificates/reports reviewed and certified by TPI/BHEL shall be submitted to BHEL as documentation package.

4. All type test reports submitted shall not be older than 5 yrs from the date of purchase order.

5. Any project/customer specific requirements which shall be notified have to be fulfilled by the vendor at the time of execution of order.

	Item : UNIVERSAL HAND HELD CALIBRATOR 

	
	
	
	
	
	
	
	
	
	
	
	

	1.0
	FINAL INSPECTION & TESTING

	1.1
	UNIVERSAL HAND HELD CALIBRATOR
	PHYSICAL VERIFICATION & MARKING CHECK
	MAJOR
	VISUAL
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION CHECK
	√
	2
	--
	1
	

	1.2
	
	PERFORMANCE
	MAJOR
	VERIFY
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	CERTIFICATE OF CONFORMANCE
	√
	2
	--
	1
	

	1.3
	
	EXPLOSION PROOF
	MAJOR
	VERIFICATION
	FOR ONE SAMPLE OF APPLICABLE DESIGN 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	EXPLOSION PROOF CERTIFICATE
	√
	2
	--
	1
	

	1.4
	
	INTRINSIC SAFE
	MAJOR
	VERIFICATION
	FOR ONE SAMPLE OF APPLICABLE DESIGN 
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	CERTIFICATE FOR INTRINSIC SAFE EXECUTION
	√
	2
	--
	1
	

	1.5
	
	GUARANTEE PERFORMANCE
	MAJOR
	REVIEW
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	GUARANTEE CERTIFICATE
	√
	2
	--
	1
	

	2.0
	PRESERVATION & PACKING

	3.1
	COMPLETE ASSEMBLY
	PACKING & PRESERVATION
	MAJOR
	PACKING
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	PACKING LIST
	√
	2
	--
	1
	


NOTE:-

1. This standard MQP should be read along with specification (latest revision), approved drawings & approved data sheet.

2. Drawing/data sheet shall prevail over quality plan for contradiction if any between quality plan and drawing/specification.

3. All test certificates/reports reviewed and certified by TPI/BHEL shall be submitted to BHEL as documentation package.

4. All type test reports submitted shall not be older than 5 yrs from the date of purchase order.

5. Any project/customer specific requirements which shall be notified have to be fulfilled by the vendor at the time of execution of order.

	Item : FRP CANOPY 

	
	
	
	
	
	
	
	
	
	
	
	

	1.0
	RAW MATERIALS & BOUGHT OUT ITEMS

	1.1
	Major Raw Material Glass & Polyester Resins
	MATERIAL OF CONSTRUCTION
	MAJOR
	MATERIAL TEST
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	MATERIAL TEST CERTIFICATE
	√
	2
	--
	1
	

	2.0
	FINAL INSPECTION & TESTING

	2.1
	Dimension (WXHXD)
	PHYSICAL VERIFICATION
	MAJOR
	Physical
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	10% WITNESS BY “1”

	2.2
	Workmanship
	PHYSICAL VERIFICATION
	MAJOR
	VISUAL
	Random
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	INSPECTION REPORT
	√
	2
	1
	--
	

	3.0
	PRESERVATION & PACKING

	3.1
	COMPLETE ASSEMBLY
	PACKING & PRESERVATION
	MAJOR
	PACKING
	100%
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	Approved Datasheet/ Approved Drawing/ Tech. spec.
	PACKING LIST
	√
	2
	--
	1
	


	LEGEND:  P: PERFORM,   W: WITNESS, V: TEST CERTIFICAT REVIEW.  INDICATE 1 FOR BHEL / BHEL NOMINATED INSPECTION AGENCY/END USER/END USER’S REPRESENTATIVE & 2 FOR VENDOR/SUB VENDOR AS APPROPRIATE AGAINST EACH COMPONENT /CHARACTERISTIC UNDER P, W & V COLUMNS. * FOR ITEMS MARKED ( (TICK) IN COLUMN ‘D’, TEST CERTIFICATES SHALL BE SUBMITTED TO BHEL FOR RECORDS.
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