## Sheet1
SUPPLY, ERECTION AND COMMISSIONING OF "SINGLE STAGE DUCTED EVAPORATIVE AIR-COOLING SYSTEMS FOR GENERAL HOSPITAL WARDS . Dt 5/5/08.
ENCLOSURES:. LAYOUT DRG S-2483 Rev-00,
TECHNICAL SPECIFICATIONS & BILL OF MATERIALS
Sl.No. | DESCRIPTION | Qty. | Rate Rs. | Total Cost Rs.
PREQUALIFICATION OF BIDDERS:
Tenderer shall necessarily submit all the following documents to get qualified.
i. | To submit proof for achieving annual turnover of minimum Rs.40.0 Lakhs towards supply, installation, commissioning of HVAC works in at least one financial year during the period April 2005 to March 2008.
ii. | To submit proof of satisfactorily executed as a prime contractor of at least TWO similar HVAC works of value not less than 20 lakhs each during the total period of April 2005 to March 2008.
iii. | Certificate to the effect that the tenderer is a own equipment manufacturer (OEM) / authorized dealer of Air Washer units.
A. | PACKAGED TYPE SINGLE STAGE EVAPORATIVE COOLING UNITS OF HIGH ADIABATIC EFFICIENCY: a) Weather Proofed b) Corrosion Protected c) Self Priming Pumps- total 2 Nos, 1 standby.
Aa | Male Surgical Ward- (91 X 20 X 11 feet , 60 people) -6500 CFM | 2 nos.
Ab | Female Surgical ward-(2 halls of 39X14X12 feet,20 people each)-7000 CFM | 1 no.
Ac | Male & Female Wards-(2 halls of 70X30X11 feet,100 people each)-13000 CFM | 2 nos.
Washer Section
1 | Inlet Filters: 50mm thick multilayer aluminium wire mesh viscous, dust filter designed at 2 mps for 20 microns efficiency encased in aluminium frames.
2 | HumidificationSection: Consists of a S.S.water tank, FRP Distributor with medium class internal GSS piping. The cellulose based media of 200mm thickness.
3 | Distibution system: G.I class-B perforated impinging piping on distributor.
4 | Bleed-Off:To maintain minerals concentration in water to an optimum level.
5 | To mention total Consumption of water per hr per unit.
Air Handling section
1 | Centrifugal fan: Farward curved dynamically balanced heavy duty centrifugal blower with 16G scroll mounted mounted on shaft and self- aligning ball bearing.
2 | Fan bearings shall be provided with grease/oil "feeder Units" to ensure lubrication.
3 | Motor: Totally enclosed 3 Ph 440V eletric motor of reputed ISI make only.
4 | Drive: Taper-lock (Fenner make only) V-Belt pullys and belts.
5 | Taper lock V-belt driven and driver pulleys
6 | Noice Level: Not more than 80 db measured at a distance of 1 mtr from machine.
Tank & Pump section
1 | Pump: 1 working and 1 standby -monoblock motor driven type.
2 | Tank: 18G Stainless Steel (SA-304 spec) with necessary class-B valves and fittings and "B" class internal piping
3 | Screen: 12 mesh brass in S.S frame.
4 | Float Valve: Highly reliable float with plastic ball.
5 | Plumbing: G.I / HDPE class-B
Casing :
1 | Material:Roof,Front and side panels-16G Prepainted GSS outside and plain 16G GSS inside duly 25 mm thick P.U.F insulated.
2 | Finish: 2 coats epoxy with 2 coats synthetic enamel paint.
3 | Exhaust gravity louers with insect screen
B | Low- Side Works: G.I ducting: Refer Drg S-2483 Rev-00
Ducting design to ensure equal distribution of air at all parts of the area.
1 | 22/24G including steel supports | 4920 SFT
2 | Thermal insulation of exposed duct with thermocol sand cement plaster | 1820 SFT
3 | Supply air grills: Aluminium 6"SAG supply air grills with VCD | 65 SFT
4 | Duct Dampers | 65 SFT
5 | Control panels and remote operating units with 30 meters wiring and laying. | 5 Nos.
6 | Thermal insulation of exposed duct with thermocol sand cement plaster | 2360 SFT
7 | Duct Dampers | 35 SFT
Prove Out of system:
1 | Payment shall be made only after successful AIR BALANCING carried out.
2 | Noice Level: Not more than 80 db near machine.
3 | Not very high air velocities that result in noice at Plenum and Ducting.
C | Design Charges | Lumpsum
D | Labour charges for erection, testing and commissioning charges | Lumpsum
Note:Payment for low side works: on actual measurements.
Taxes
GRAND TOTAL

## Sheet3
BHARAT HEAVY ELECTRICALS LIMITED
TENDER FOR
HVAC WORKS FOR 02-SUPER HEAVY BAY AIR CONDITIONING ROOM AT R.C.PURAM , HYDERABAD - 502 032
VOLUME -1 : TECHNICAL SPECIFICATIONS VOLUME-2 BILL OF QUANTITIES
VOLUME -1. TECHNICAL SPECIFICATIONS
TECHNO-COMMERCIAL BID
1. SPECIFICATIONS FOR AIR CONDITIONING SYSTEM
2. LIST OF APPROVED MAKES
3. LIST OF DOCUMENTS / REGISTERS TO BE MAINTAINED
1. SPECIFICATIONS FOR AIR CONDITIONING SYSTEM
Sl.No. | DESCRIPTION | OFFERED | DEVIATION
BIDDING QUALIFICATIONS (TENDERER QUALIFICATIONS / CAPABILITIES) BIDDER TO NOTE AND FURNISH THE RELEVANT DATA FOR QUALIFYING THE FOLLOWING (TO BE FURNISHED BY THE BIDDER)
Attested Xerox copies of certificates of tenderer in his name in support of achieving the following in the last FIVE financial years from 2000 to 2005.
i. | Total annual turnover experience certificate in supply, installation, commissioning of HVAC works of value Rs.350 lakhs in any one financial year.
ii. | The tenderer should have satisfactorily executed as a prime contractor of at least one similar work of value not less than 100 lakhs during the period 2000 to 2005.
iii. | Certificate to the effect that the tenderer is a own equipment manufacturer (OEM) / authorized dealer of package units/split units with necessary past performance as per data indicated herein above.
A. | AIR COOLED PACKAGE AIR CONDITIONER UNIT
1 | SCOPE:The scope of this section comprises supply, erection, testing and commissioning of self-contained air cooled package air-conditioning units and auxiliaries conforming to these specifications and in accordance with the drawings.
2 | PACKAGE UNITS:
Air cooled, floor mounted free standing package unit shall be provided with scroll/reciprocating compressor complete with vibration isolators & factory installed controls (like HP & LP cutouts, inter locking of Fan & Compressor, Thermostat with selector switch etc) & accessories including wiring. Efficient cooling coil shall be selected for low velocity with 3/8"/1/2" OD copper tubing having extended aluminium fins. Hydraulic expansion of tubes assures tight bonding between tubes & fins for high heat transfer. Tubes shall be arranged in a staggered design for best air contact thus giving low bypass. The cooling coil circuits are fed with liquid refrigerant through the thermostatic expansion valve and a distributor Blower of an evaporating unit shall be statically and dynamically balanced and shall be selected to give required airflow as identified in the drawings. Filters shall be minimum 25mm thick synthetic type or equivalent wire aluminium frame. Drain pan shall be of 18 gauge insulated with expanded polyethylene sheet. Casing shall be as per the manufacturer's recommendation factory painted to provide better protection against rusting.
Remote air cooled condensing unit shall have to be most efficient condenser coils made out of copper tubing with extended aluminium fins. Tubes shall be arranged in a stag-gered design for better efficiency. Condenser fans shall be selected to operate quietly for required CFM to keep condensing temperature low. The compressor may be in the indoor unit or with the outdoor unit, but, it should be capable of operating continuously even at high ambient of 460C (1150 F).
Interconnected refrigerant copper hard drawn piping between outdoor unit & indoor unit shall be of heavy gauge complete with thermostatic expansion valve, liquid line strainer, drier, shut off valves, high & low pressure gauges including insulated suction line. 25mm thick neoprene rubber pads shall be supplied for each indoor / outdoor units. The units shall be tested in accordance with IS: 1391.
3 | INSTALLATION:
The indoor units shall be mounted on ribbed rubber pads for vibration isolation. The outdoor unit shall be installed with a steel base frame along with cushy foot mounting vibration isolation units. The refrigerant pipes & interconnecting cables & wires shall be neatly & firmly installed on 16 SWG cable trays. The cable trays shall be rigidly supported from walls/slabs. Care shall be taken to avoid possibility of damage to cable/wires insulation due hot refrigerant pipes. The contractor shall supply the required charge of refrigerant, lubricant and other consumables, for commissioning and testing of the equipment. The vendor has to provide complete supporting arrangements, auxillary steel brace frame etc., to avoid any civil foundations works for indoor and outdoor units.
All the equipment shall be thoroughly tested and checked for leaks. All safety controls shall be suitably set and a record of all setting shall be furnished to the Engineer in charge.
4.0 | SPLIT UNITS (NOT IN THE SCOPE FOR THE PRESENT SCHEDULE):
5.0 | TESTING:
Unit capacity in tons Refrigeration, shall be computed from the temperature readings and air-flow measurements. Flow measurements shall be preferably by a hot-wire anemometer or a velometer. Computed results shall conform to the specified capacities and the power consumption shall conform to the figures furnished by the manufacturer. Further, Bidder shall furnish all supporting calculations and method of testing likely to be conducted for the performance and capacity tests for the Package Units at manufacturing premises as per standards & procedures being adopted at the time of submitting the tender with complete facilities available for type test required to be witnessed by the clients Engineer and Consultants to give clearance of Package units after satisfactory and successful completion of tests atleast on one each type of units offered for the project. Further Bidder shall also adhere and prove the installation performance at site to meet the required design parameters for the entire system. Methodology likely to be adopted also to be furnished by the Bidder at installation certification stage only this will eligible for final clearance of payment against performance of the AC system which forms the part of the scope of work.
6.0 | PAINTING:
Shop coats of paint that have become marred during transportation or erection shall be cleaned off with mineral spirits, wire brushed and spot primed over the affected areas, then coated with two coats of enamel paint to match the finish over the adjoining shop-painted surfaces.
7.0 | CONDENSATE & DRAIN PIPING:
7.1 | All pipes to be used for condensate drain shall be approved make and fittings as per BIS 4736 or galvanized steel class B (medium class) conforming to relevant BIS codes.
7.2 | All jointing in the pipe system shall be by screwed fittings using non-hardening lubricant as sealing material and/or by screwed flanges using 3mm 3 ply rubber gaskets. Pipe threads and flanges shall be as per BS 534 and BS 4504
7.3 | All pipe supports shall be mild steel, thoroughly cleaned and given on primary coat of red oxide paint before being installed.
7.4 | Fittings shall be galvanized steel 'Medium Class' malleable casting of pressure rating suitable for the piping system. Flanges shall be of approved make. Supply of flanges shall include bolts, washers, gaskets as required sufficient number of flanges and unions shall be provided for future cleaning and servicing of piping. Tee-off connections shall be through equal or reducing tees. All equipment and valve connections, or connections to any other mating pipe shall be through unions/screwed flanges upto 50 mm dia and through screwed flanges for larger diameters, or as required for the mating connections.
7.5 | All condensate drain piping shall be insulated as per the section 'Insulation' Cold water piping within the building may also be insulated.
7.6 | After the piping has been installed, tested and run for atleast three days of eight hours each, all piping and pipe supports shall be painted with one coat of red oxide paint & two finish coats of 3 mils each of approved color of synthetic enamel paint conforming to IS 2379
7.7 | The direction of flow of fluid in the pipes shall be visibly marked with identifying arrow.
8.0 | REFRIGERANT PIPING:
a | All refrigerant pipes and fittings shall be type L' hard drawn copper tubes and wrought copper fitting suitable for connection with silver solder phos copper or as per Manufacturers recommendations
b | All joints in copper piping shall be sweat joints using low temperature brazing and/or silver solder. Before jointing any copper pipe or fittings, its interior shall be thoroughly cleaned be passing a clean cloth via wire or cable through its entire length. The piping shall be continuously kept clean of dirt etc. while construction the joints. Subsequently, it shall be thoroughly blown out using carbon-dioxide/nitrogen
c | Refrigerant lines shall be sized to limit pressure drop between evaporator and condensing unit to less than 0.2 kg per Sq.cm.
d | Removable type combination drier and filter shall be installed in liquid line of the refrigeration system incorporating a three way valve bypass. After ninety days of operation, liquid line drier and filter cartridges must be replaced by contractor at actual cost to be borne by owner.
e | After the refrigerant piping installation has been completed the refrigerant piping system shall be pressure tested using, Freon mixed with nitrogen/carbondioxide at a pressure of 20 Kg per Sq. cm (High side) and 10 Kg per Sq. cm (Low side) pressure shall be maintained on the system for a minimum of 12 hours. The system shall then be evacuated to a minimum vacuum of 70 cm. of mercury and held for 24 hours, during which time, change in vacuum shall not exceed 12 cm of mercury. Vacuum shall be checked with vacuum gauge
f | The contractor shall provide all materials, tools, equipment, instruments, services and labour required to perform the test.
g | Complete certified report shall be submitted for evaluation and approval to Engineer in charge. Upon approval, four copies of the balancing report shall be submitted with complete drawings and documents
9.0 | TESTING & BALANCING
a | All piping shall be tested to hydrostatic test pressure of atleast two and half times the maximum operating pressure, but not less than 24 hours. All leaks and defects in joints revealed during the testing shall be rectified and gotten approved at site
b | Piping repaired subsequent to the above pressure test shall be retested in the same manner
c | System may be tested in sections and such sections shall be securely capped, then retested for entire system.
d | The contractor shall give sufficient notice to all other agencies at site, of his intention to test a section or sections of piping and all testing shall be witnessed and recorded by Owner's site representative.
e | The Contractor shall make sure that proper noiseless circulation of fluid is achieved through all coils and other heat exchange equipment in the system concerned. If proper circulation is not achieved the contractor shall rectify the defective connection. He shall bear all expenses for carrying out the above rectifications, including the tearing up and refinishing of floors and walls as required.
f | The Contractor shall provide all materials, tools, equipment, instruments, services and labour required to perform the test.
g | Complete certified report shall be submitted for evaluation and approval to Engineer in charge. Upon approval , four copies of the balancing report shall be submitted with complete drawings and documents.
B | FANS
1.0 | SCOPE
Scope of this section comprises of supplying, erection, testing and commissioning of following type of fans.
a | Centrifugal Fans SISW/DIDW
b | Inline fans (Vane axial/Tube axial)
c | Propeller fans
The above fans shall be as indicated on drawings and mentioned in schedule of quantities.
2.0 | CENTRIFUGAL FANS:
2.1 | Scroll:
Forward curved dynamically balanced heavy-duty centrifugal blower with 16O scroll mounted on shaft and self-aligning ball bearings.
2.2 | Impeller:
The impeller, pulley and housing shall be statically and dynamically balanced. FAN velocity shall not exceed 1800 FPM at a maximum fan speed of 1000 RPM.
2.3 | Shaft:
Shaft shall be constructed of SAE 1040 steel turned, ground and polished Shaft shall not pass through first critical speed through the full range or specified fan speeds.
2.4 | Bearings:
The bearing shall be self-aligning, heavy-duty ball, roller or sleeve bearings Bearing shall be selected for quiet operation and shall be grease pack, pillow block type.
2.5 | Inlet guard:
Inlet guard shall be spun to have a smooth contour. Inlet screen if provided shall be of galvanized wire mesh of 25 mm square.
2.6 | Base Plate:
Base plate shall be provided for each fan Base for both fans and motor shall be built as an integral part and shall be mounted on a concrete foundation through cushy foot mountings for vibration isolation The concrete foundation shall be at least 150 mm above the finished floor level and shall be further isolated from structural floor through 50 mm thick layers of sand all around, topped with bitumen.
2.7 | Motor:
Fan motor shall be of squirrel cage type totally enclosed fan cooled motor, suitable for 415 ± 10% volts, 50 Hz, 3 phase. Horse power indicated on the name plate of motor shall be more than brake horse power by at least 10%. Motor R.P.M. shall not exceed 1500 RPM. The fan motor combination selected for the particular requirement shall be of the most efficient type (i.e smallest horse power) so that power consumption and noise level may be minimised.
Motor shall be outside the fan section, which will be independently covered & weather protected.
2.8 | Drive:
These fan shall be provided with V belts All belts shall be selected for 150% rated HP All V-belt shall be supplied with removable belt guards that do not impede the air flow to the fan inlet. There shall be a minimum of two belts per drive.
2.9 | Vibration Isolation:
Fan with motor shall be mounted on a concrete foundation through vibration isolation cushy foot mounting as per section
3.0 | IN-LINE FANS:
3.1 | In-line fans shall be Designed tube Axial flow, belt driven complete with motor, belt guard, motor mount and vibration isolation type suspension arrangement
Shall be constructed of 14 gauges sheet steel. Fan casing, motor mount and straightening vane shall be of welded steel construction. Motor mounting plate shall be minimum 20 mm. thick and machined to receive motor flange. Casing shall be provided with two Nos. wide hinged doors which open easily. Inspection doors with handle and neoprene gasket shall also be provided. Casing shall have flanged connection on both ends for ducted applications. Support brackets for ceilings suspensions shall be welded to the casing for connection to hanger bolts. Straightening vanes shall be aerodynamically designed for maximum efficiency by converting velocity pressure to static pressure potential and minimizing turbulence. Casing shall be bonderized, primed and finish coated with enamel paint.
3.2 | Rotor:
Hub and blades shall be cast aluminium construction. Blades shall be die formed Aerofoil section for max. Efficiency and shall vary in twist and width from hub to top to effect equal air distribution along the blade length. Fan blades mounting on the hub shall be statically and dynamically balanced. Maximum clearance between blade tip and fan housing at the specified duty blade setting shall be 5 mm. Rotor blades shall be whirl tested to speed of 25% above the design operating speed and certification of the test shall be provided by the manufacturer. Extended grease leads for external lubrication shall be provided. Rotor shall be statically and dynamically balanced. The fan pitch control shall be manually readjusted at site upon installation for obtaining actual airflow valves as specified and quoted. The impeller blade shall be of adjustable type blade.
3.3 | Motor
Shall be squirrel cage, totally enclosed, fan cooled standard round frame, constant speed, continuous duty, single winding, suitable for 415 +/- 10% volts, 50 cycles, 3 phase power supply, provided with class "B" insulation. Motor nameplate horsepower shall be more than brake horsepower by a minimum of 10%. Motors shall be specially designed for quiet operation and motor speed shall not exceed 1500 RPM. For maximum efficiency or minimum horsepower. Motor conduit box shall be mounted on exterior of a casing, and lead wires from the motor to the conduit box shall be protected from the air stream by enclosing in a flexible metal conduit.
3.4 | Drive;
The fan shall be provided through belt drive with adjustable motor sheave and standard sheet steel belt guard with vented front for heat dissipation. Belt shall be of the oil-resistant type.
3.5 | Vibration Isolation:
The assembly of fan and motor shall be suspended from the ceiling by spring type vibration isolators
Accessories;
The following accessories shall be provided with all fans:
i. | Outlet cone for static pressure regain
ii. | Inlet cone.
iii. | Fan silencers if required
Fan shall be factory assembled and shipped with all accessories factory-mounted.
4.0 | PROPELLER FANS:
Propeller fans shall be approved make direct-drive, three or four blade type mounted on a steel mounting plate with orifice ring.
4 1 | Mounting Plate:
Shall be steel construction, square with streamlined venturi inlet (reversed for supply applications) coated with baked enamel finish, the mounting plates shall be of standard size, constructed of 12 to 16 gauge sheet steel depending upon the fan size. Orifice ring shall be correctly formed by spinning or a stamping to provide easy passage of air without turbulence and to direct the air stream
4.2 | Fan Blades:
Shall be constructed on aluminium or steel Fan hub shall be of heavy welded steel construction with blades bolted to the hub Fan blades shall be quiet in operation and shall be statically and dynamically balanced at the factory
4.3 | Shaft:
Shall be of steel, accurately ground and shall be of ample size for the load transmitted, and shall not pass through first critical speed thru the full range of specified fan speeds.
4.4 | Motor:
Shall be standard (easily replaceable) permanent split capacitor or shaded pole for small sizes, totally enclosed with prelubricated sleeve or ball bearings, designed for quiet operation with a maximum speed of 900 RPM for fans of 380 mm. dia or larger and 1450 RPM for fans 300 mm dia or smaller Motors for fans 600 mm dia and larger shall be suitable for 415 +/- 10% volts, 50 cycles, 3 phase supply, and for fans less than 60 cms. dia shall be suitable for 230 +/- 6% volts, 50 cycles, single phase power supply, and shall be suitable for either horizontal or vertical service, as indicated on Drawings and in Schedule of Quantities.
4.5 | Accessories:
The following accessories may be required and provided with propeller fans as indicated in BOQ
i. | Wire guard on inlet side, and birdscreen at the outlet.
ii. | Gravity operated MS spray galvinised louver shutters built into a frame.
iii. | Regulators for controlling fan speed for single phase fan motors.
5.0 | PERFORMANCE DATA:
All fans shall be selected for the lowest operating noise level. Capacity rating, power consumption with operating points clearly indicated, shall be submitted, and verified at the time of testing and commissioning of the installation
6.0 | TESTING:
Capacity of all fans shall be measured by a hot wire anemotherm Measured air flow capacities shall conform to the specified capacities and quoted ratings. Power consumption shall be computed from measurements of incoming voltage and input current.
C | AIR DISTRIBUTION SYSTEM:
1.0 | GENERAL:
Supply, fabrication, installation and testing of all sheet metal/aluminium ducts & supply, installation, testing and balancing of all grilles, registers and diffusers, in accordance with these specifications and the general arrangement shown on the drawings and as per Bill of quantities.
Ductwork shall mean all ducts, casings, dampers, access doors, joints, vanes, stiffeners, hangers and supports etc.
All ducts shall be fabricated from galvanised steel sheets of the following thickness as indicated in schedule of quantities & as described in the IS:655 with latest edition.
2.0 | RECTANGULAR DUCT:
Dim of Ducts Gauge G.I Gauge Alu Type of Joints Type of Bracings
Upto 600 24 22 G.I Flange at 2.5 Center Cross Bracings
601 to 750 24 22 25X25 X3 mm angle with 6mm dia nuts&bolts 25X25X3mm MS angle iat 1500mm from joints
751 to 1000 22 20 25X25X3mm MS angle with 6mm nuts&bolts 25X25X3mm MS angle bracing at 1500mm from joints.
1001 to 1500 22 20 40X40X5 with 8 dia nuts&bolts 40X40X3 angle bracing at 1500 mm from joints
1501 to 2250 20 16 50X 50X3 mm angle braced diagnolly with 10mm dia nuts&bolts at 125 center 40X40X3 angle bracing at 1200 from MS angle diagnonal bracing.
2250 and above 18 14 50X50X6 angle,10mm bolts & nuts at 125 center 50X50X3mm angle bracing at 1200mm from joints or 50X50X3 angle diagnol bracing
Sheet metal ducts shall be fabricated out of galvanized steel sheets conforming to BIS 655, BIS 277, BIS 737 & SMACNA Sheets used shall be produced by Hot dip process and galvanizing shall be Class VIII- Minimum Average Coating 120 gm/sq.m as per BIS 277: 1992.
3.0 | HANGERS FOR DUCT
Duct size (MM) spacing(M) Size of MS angle(mmXmm) Size of rod dia (mm)
Upto 750 2.5 40X3 10
751 to 1500 2 40X3 12
1501 to 2250 2 50X3 15
2251 to above 2 50X3 15
4.0 | FABRICATION:
All ducts shall be fabricated and installed in workman like manner, generally conforming to IS 655. Round exposed ducts shall be die formed for achieving perfect circle configuration
a | Ducts so identified on the drawings shall be acoustically lined with thermal insulation as described in the section 'Insulation' and as indicated in schedule of quantities Duct dimensions shown on drawings are overall sheet metal dimensions inclusive of acoustic lining, where required and indicated in schedule of quantities.
b | Ducts shall be straight and smooth on the inside with neatly finished joints. All joints shall be made air tight.
c | All exposed ducts within conditioned spaces shall have slip joints - no flanged joints. The internal ends of slip joints shall be made in the direction of air flow.
Exposed ducts, where required or as indicated in Schedule of quantities, shall be painted with two coats, of enamel paint of approved colour. Ducts and accessories within ceiling spaces, visible from air conditioned areas shall be provided with two coats of mat black finish paint.
d | Changes in dimensions and shape of ducts shall be gradual Curved elbows, unless otherwise indicated, shall have a centre line radius equal to one and a half times the width of the duct. Air turns shall be installed in all vanes, arranged to permit the air to make the turn without appreciable turbulence. Suitable vanes shall be provided in duct collar to have uniform/ proper air distribution
e | Ducts shall be fabricated as per details shown on drawings. All ducts shall be rigid and shall be adequately supported and braced where required with standing seams, tees, or angles of sample size to keep the ducts true to shape and to prevent bulking, vibration or breathing
f | All sheet metal connections, partitions and plenums required to confine the flow of air to and through 18g GI/16 gauge aluminium, thoroughly stiffened with 25mm x 25mm x 3mm angle iron braces and fitted with all necessary doors as required to give access to all parts of the apparatus Access Doors shall be not less than 45cm x 45cm in size.
g | Ducts required for exhaust of air consisting of corrosive fumes shall be fabricated of 4 mm thick polypropylene sheets All joints shall be leak proof & sealed with suitable sealent of GE make. Ducts shall be of cylindrical shape with smooth bends to avoid deposit of foreign bodies within ducts. No accessories shall be installed within ducts. The exhaust shall be through lip extraction system at fume generating surfaces.
5.0 | INSTALLATION:
All ducts shall be installed generally as per the drawings and in strict accordance with approved shop drawings to be prepared by the Contractor.
i | The Contractor shall provide and neatly erect all sheet metal work as may be required to carry out the intent, of these specifications and drawings. The work shall meet with the approval of Owner's site representative in all its parts and details
ii | All necessary allowances and provisions shall be made by the Contractor for beams, pipes, or other obstructions in the building, whether or not the same are shown on the drawings. Where necessary to avoid beams or other structural work, plumbing or other pipes, and/or conduits, the ducts shall be transformed, divided or curved to one side, the required area being maintained, all as per the site requirements.
iii | If a duct cannot be run as shown on the drawings, the contractor shall install the duct between the required points by any path available, in accordance with other services and as per approval of Owners site representatives.
iv | All duct work shall be independently supported from building structure. All horizontal ducts shall be rigidly and securely supported, in approved manner with trapeze hangers formed of MS rods and angle iron under ducts at not greater than 2 meter centres. All vertical duct work shall be supported by structural members at each floor. Air conditioning contractor shall supply and install 50mm cube MS boxes with 10mm dia steel rod passing through box, all given two coats of redoxide paint, the MS rod tied with reinforcement bar at point of suspension shall be neatly exposed and opening subsequently filled with plastic compound after duct hangers are installed.
If duct is passing through in such areas where space between ceiling slab to false ceiling is more than 1500 mm than duct should be supported by wall mounted brackets of 40 x 40 x 3 mm angle
v | Ducting over furred ceiling shall be supported from the slab above, or from beams, after obtaining approval of Owner's site representative In no case shall any duct by supported from false ceiling hangers or be permitted to rest on false ceiling. All metal work in dead or furred down spaces shall be erected in time to occasion no delay to other contractors on the building
vi | Where metal ducts or sleeves terminate in wood work, tight joints shall be made by means of closely fitted heavy flanged collars. Where ducts pass through brick or masonry opening and wooden frame work shall be provided within the opening and crossing ducts provided with heavy flanged collars on each side of wooden frame work, so that duct crossing is made leak-proof
vii | All ducts shall be totally free from vibration under all conditions of operation. Whenever duct work is connected to fans, air handling units or blower coil units that may cause vibrations in the ducts, ducts shall be provided of closely woven, rubber impregnated double layer asbestos/canvas or neoprene coated fibre glass fire resistant flexible connection. The flexible connections located close to the unit, in mutually perpendicular directions. The flexible sleeve at least 10cm long securely bonded and bolted on both sides. Sleeve shall be made smooth and the connecting duct work rigidly held by independent supports on both ends. The flexible connection shall be suitable for pressures at the point of installation.
viii | Air conditioning unit and exhaust fans shall be connected to duct work by inserting at air inlet and air outlet a double canvass sleeve. Each sleeve shall minimum 150 mm securely bolted to duct and the connecting duct work rigidly held in line with unit inlet or outlet
6.0 | SPUTTERS AND DAMPERS:
All dampers shall be opposed blade type dampers of robust construction and tight fitting. They shall be made of G.S. sheet minimum 16 g thick and shall have brass bushes. The design, method of handling, and control shall be suitable for the location and service required.
Dampers shall be provided with suitable links, levers and quadrants as required for their proper operation control or setting devices shall be made robust, easily operatable and accessible through suitable access doors in the ducts. Every damper shall have an indicating device clearly showing the damper position at all times Handles will be provided with extended arms to account for insulation thickness.
Dampers shall be placed in ducts and at every branch supply or return air duct connection, whether or not indicated on the drawings, for the proper volume control and balancing of the system.
7.1 | FIRE DAMPER:
All Supply/Return air duct or path at Package Unit room wall or slab crossing shall be provided with fusible link / smoke censor integrated type fire damper as specified in BOQ. The fire rating shall be of 90 minutes fire damper blades and outer frame shall be formed of 1.6 mm galvanised sheet steel. The damper blade shall be pivoted spindles in self lubricated bronze bushes, stop seals shall be provided on top and bottom of the damper housing made of 16g galvanised sheet steel. Side seal shall be provided to preventing fire leakages
7.2 | FLEXIBLE DUCT CONNECTION :
The Flexible Connection should be made of TF quality fire retardant double canvas or imported fabric of fibreglass weave having silicone rubber coating, as mentioned in the schedule of quantities. Flexible connections shall be air tight & water proof and withstand high temperature application,' non flammable type and does not support combustion. There shall be extruded Angle aluminum frame at both ends for connection
8.0 | MOTOR1SED COMBINATION SMOKE & FIRE DAMPER :
All supply/return air duct or path at AHU room wall or slab crossing shall be provided motorised combined smoke and fire damper The fire rating shall be of 90 minutes fire damper blades and outer frame shall be formed of 1.6mm galvanised sheet steel. The damper blade shall be pivoted spindles in self lubricated bronze bushes, stop seals shall be provided on top and bottom of the damper housing made of 16g galvanised sheet steel. Side seal shall be provided to preventing fine leakages. Fire damper shall be kept open during normal mode with the help of 230 V operated electric actuators spring to providing maximum air passage without creating any noise or actuated either through electric actuator or through UL stamped electro-thermal link. The actuator shall be energized with the help of a single from smoke detector installed in AHU room / RA duct/damper. The fire damper shall also close due to temp rise in SA Ducts through the electric temp sensor factoy set at 165 deg F, micro switches with bakelite base will be provided to stop fan motor & give open & close singnal at remote panel in case of motorised damper
ACTUATOR:
In case of motorised smoke -cum-fire damper it shall have its own panel which will incorporate necessary circuit required to stop down voltage available from UPS or emergency power supply to show the status of damper (open or closed), to allow remoting testing of damper & indication in event of damper clouser due to signal from smoke sensor/temp sensor & reset button Additional terminal will be provided to have single (sound beep or visual)in central control room. The fire damper shall be mounted in fire rated wall with a duct sleeve 400mm/500mm long depending upon the wall thickness. The sleeve shall be factory filled of fire damper the joints at sleeves end shall be slip on type minimum thickness of GI sheet shall be 18g. The fire damper shall be installed in accordance with the installation method recommended by the manufacturer
9.0 | SUPPLY AND RETURN AIR GRILLES:
Supply and return air grilles shall be MS or anodized extruded aluminium construction with individually adjustable bars as shown on drawings and indicated in schedule of quantities. Supply air grilles shall be generally double deflection type, with removable key operated volume control dampers. Return air grilles shall be generally double deflection type similar to supply air grilles but without dampers. All supply and return air grilles behind wooden grilles shall be single deflection type with one way bars only, the supply air grilles being provided with removable key operated volume control dampers. Mild steel supply and return air grilles shall be factory coated with rust resistant primer and shall be finished with two coats of paint as per client's choice. Aluminium supply and return grilles shall be powder coated and to have colour of client's choice or extruded aluminium as per bill of quantities
10 | SUPPLY AND RETURN AIR DIFFUSERS:
Supply and return air diffusers shall be shown on the drawings and indicated in schedule of quantities. The supply air diffuser shall be provided with removable key operative volume control dampers. Mild steel diffusers/dampers shall be factory coated with rust resistant primer. These shall be finished with two coats of paint as per client's choice Aluminium supply and return air diffusers shall be powder coaled and to have colour of client's choice or shall be extruded aluminium
ii | Round or Rectangular Diffusers:
Supply/return air linear diffuser shall be MS or Extruded aluminium construction, square, rectangular, or round diffusers with flush fixed pattern or adjustable flow pattern. Diffusers for different spaces shall be selected in consultation with the Architect/Consultants Supply air diffusers may be equipped with fixed air-distribution grids, removable key-operated volume control dampers, and antismudge rings as per requirements of schedule of quantities.
ii | Linear Supply air/ Return Air Grilles:
This shall be extruded aluminium construction with fixed horizontal bars at 15 dig inclination and flange on both side. The thickness of fixed bar louvers shall be at least 5.5mm & angle shall be 20mm/30mm inside The grilles shall be suitable for concealed fixing volume control damper of extruded. Aluminium construction with black anodised finished shall be provided in SA duct collars
11.0 | LINEAR DIFFUSER ;
Liner diffuser shall be extruded aluminium construction multislot type with air pattern controlled provided in each slot. Supply air diffusion shall be provided with volume damper in each slot of the supply air diffuser. Plenum shall be provided for each supply air diffuser.
The Material of Grilles shall be as follows:
i. | Al1 grilles shall be selected in consultation with the Architect/Consultant.
Different spaces shall require horizontal or vertical face bars, and different width of margin frames.
ii. | All grilles shall have a soft, continuous rubber gasket between the periphery of the registers and the surface on which it has to be mounted. The effective area of the registers shall not be less than 75 percent.
iii. | Grilles shall be adjustable pattern as each grille bar shall be pivotable to provide pattern with 0 to 100 deg horizontal arc and upto 30 deg C deflection up or down Bars shall hold deflection settings under all conditions of velocity and pressure. Extruded aluminium grilles shall have fixed bars.
iv. | Bars longer than 45cm shall be reinforced by set-back vertical members of approved thickness.
The material thickness of grills, diffuser,damper shall be as follows :
Diffuser MS Aluminium
a) | Frame 20gauge 18gage
b) | Louvers 20 18
Grills:
a) | Frame Louvers 20,26 18,24
V.C. Damper :
a) | Frame 20 18
b) | Louver 26 24
v | Fresh air intake and Extract louvers:
All the louvers shall be rain protection type and shall be fabricated from extruded aluminium section. The louvers shall additionally be provided with heavy duty expanded metal (aluminium - alloy) bird screen.
12.0 | TESTING & BALANCING:
After the installation of the entire air distribution system is completed in all respects, all ducts shall be tested for air leaks before painting the interiors of conditioned spaces air distribution system shall be allowed to run continuously for 48 hours for driving away any dust or forein material logged within ducts during installation.
D | THERMAL/ACOUSTIC INSULATION. GENERAL:
Scope of this specification comprises of supplying, installing, testing and commissioning of insulation on duct, pumps, chilled water piping, chillers, expansion tank, Package Unit room and duct lining.
1.0 | DUCT INSULATION:
Resin bonded, glass wool, prelaminated with aluminium foil. The thermal conductivity of glass wool shall not exceed 0.024 Kcal/hr sqm deg C (0.19 BTU in/Hr Sq ft deg F at 10 deg C - mean temperature and density shall not be less than 48 kg/m3.
1.1 | Thickness of Insulation:
a | For Duct passing through return air areas-25mm
b | For Duct passing through non air conditioned space--50mm
c | Treated fresh air duct--50mm
d | For exposed duct---50mm
1.2 | Application: (For unexposed duct)
- Clean the surface of duct and apply coal of Black Japan paint of approved make applied @ 7 Sq mt./Kg.
- Fix the insulation material of required thickness before adhesive dries up. All longitudinal joint will have an over lap of minimum 50 mm followed by covering firmly by 75 mm width aluminium sticking tape to seal all transverse & longitudinal joints.
Where the duct is exposed to atmosphere material shall be same as for ducts not exposed to atmosphere but without aluminium foil
Application: (For exposed duct)
a. | Cleaning the surface of ducts with wire brush to remove dirt, rust etc.
b. | Applying a coat of adhesive.
c. | Fixing the glass wool insulation and tied with PVC strap of 25mm width
d. | Cover the insulation with fire retardant quality polythene lined hessian of 500g and seal the joint with black Japan
e. | Fixing 24 x 3/4" Hexagonal wire netting tied with G.I. wire.
f | Finally applying sand cement plaster in ratio 1:3 in two layers each 10mm thick.
g. | Paint it to required colour with brush.
2.0 | ACOUSTIC LINING OF PACKAGE UNIT ROOM AND LINING OF DUCTS:
For acoustic lining of Package Unit room/plant room and duct lining material shall be resin bonded glass wool of density not less than 32 kg/m3. All duct upto a distance of 5m from Pleanum outlet or as shown in the drawing shall be acoustically lined from inside
2.1 | Application:
2.1.1 | Duct Lining:
Clean the inner surface of duct which is to be lined with wire brush to remove the dirt.
Fixing GI frame Z section of 24 g of 25 mm x 25 mm x 25 mm size at 600mm distance screwed with the duct and making size as per requirement
apply a Black Japan paint over the Frame/duct.
The adhesive shall be non flammable, odorless and having vapour barrier property
Fixing insulation material of specified thickness and covered with R. P Tissue paper and then covering the material with 28 g perforated aluminium sheet having 2 mm dia perforation at 3 mm enter to center distance with the help of self tapping screws and shall be neatly finished to give true surface finish
Specification for acoustic lining of Package Unit Room Walls/ceiling :
For acoustic lining of Package Unit Room insulating material shall be resin bonded glass wool of density 32kg/m3 and thickness 25 mm/50mm
Clean wall/ceiling surface which is to be acoustically lined
Fixing GI frame Z section of size 25 x 45 x 25 x mm, or of equal insulation thickness as specified, to the wall/ceiling with screw/bolts.
Apply a 2 coats of Black Japan Paint on wall/ceiling
Resin bonded glass wool of 25mm/50mm thickness shall be fixed in GI frame of 600mm x 600mm dimension, covered with R.P Tissue
Covering the material with 24 gauge perforated aluminium sheet should have 3mm dia perforation at 4 to 6mm center to center with self tapping screws.
- All joints of perforated aluminium sheet should be covered with 20 mm aluminium curved beading
BASIS OF DESIGN
AC REQUIRED FOR STATOR WINDING HALL / EM SHOP – 40M X 28M X 5M H
1 | Area To be airconditioning 12051 SFT (40M X 28M X 5M)
2 | Height of the hall (Below false ceiling) 15.0 Ft
3 | Out Side Condition
Summer: 41ºC Dry Bulb 25.5ºC WB 28%RH
Monsoon: 29.5ºC DB 27.2ºC WB 82% RHº
4 | Inside Conditions and requirements:
Temperature: Max. 22ºC Min 18ºC RH 55% Max.
5 | Occupancy 25 people
6 | Lighting 4KW
7 | Equipment Load 11 kW + 30 kw from brazing operations
8 | Air Changers required for P unit sizing: 20 ACHP or dehumidified air whichever is higher
9 | Exhaust from brazing process:10 to 15% as part of circulated air volume
10 | Fresh Air quantity: 15% to 20% of circulated air volume
11 | Door openings per shift: 10 to 12 and 2 shifts per day
12 | Loading & unlading mechanisms of stator assy during a month---4 to 5 operations per job per month.
13a | Special remarks
Top sliding roof for each job is envisaged to be opened atleast 4 to 5 times in a month. And the AC may be switched off during such operation.
14 | Specific AC system plan
The estimated load per peek summer is in the order of 120 TR with above design assumptions. The scheme shall normally comprised as under.
a | 10 Nos. (8 w + 2 s) Air cooled floor mounted type packaged air conditioning systems with scroll or semi hermetic reciprocating compressors with allied programmable micro processor control panel as complete with copper refregirent piping and factory fabricated and factory tested set with base frame vibration isolators, ready to commissioning basis. However, BHEL has an option to opt for stand by package units along with the main bid or may delete if not so required.
b. | Separate fresh air scheme / exhaust air scheme for brazing operations also is envisaged for any cross contamination if predicted from the user end or client may procure as an optional item along with this bid.
E | TECHNICAL DATA (TO BE FURNISHED BY THE BIDDER)
1.0 | AIR COOLED PACKAGE/SPLIT A/C UNIT:
a) | Make & Model No.
b) | Nominal cooling capacity (tons)
c) | Actual cooling capacity at specified Conditions
d) | Operating weight of indoor unit(Kg.):
e) | Operating weight of Air cooled condenser unit (Kg.)
f) | Refrigerant
g) | Nominal Air Quantity (Cfm )
h) | Compressors
i) | Type of compressor
I | Power Requirement at 100% capacity
75% capacity
50% capacity
III | Unloading mechanism details
IV | Type of Starter
V | Starting Current
VI | Running Current
j | Blower Size Motor HP
k | Condenser
No. of Fans & Fans Size Air Qty of each fan Motor HP
l) | No. of Rows Evaporator Condensers
m) | Face Area Evaporator Condensers
n) | External S.P or Evaporator fan (mm WG)
o) | Indoor Unit Dimensions
i) | 1. Length (mm)
ii) | 2.Depth (mm).
iii) | 3.Height (mm).
p) | Control Panel & Accessories
2.0 | INSULATION: DUCTING ACCOUSTIC LINING PIPING
Mfger Mtls Density 1) 2) 3)
Mean 'K' value at 50°C 1) 2) 3)
3.0 | CONTROLS:
Refrigerant
Manufacturer
Capacity
Connection size
4.0 | PROPELLER FAN
a) | Make
b) | Model
c) | Fan dia (mm)
d) | Capacity
e) | Static Pressure (mm Hg)
0 Power requirement (KW)
g) Power Supply (1 ph/3 ph)
5.0 | AIR CURTAIN :
Make
Model
Fan dia (mm)
Overall dimensions
Capacity
Static Pressure (mm Wg)
Power requirement (Watts)
Power Supply
7.0 | DAMPERS
Fire Dampers
Make
Material
Gauge
Volume Control Dampers
Make
Material
Gauge
8.0 | GRILLS/DIFFUSERS
Louveres (Make, Material & Gauge)
Make
Material
Gauge
Grilles (Make,Materials & Gage)
Make
Material
F) | Mode of Measurements:
PERFORMANCE TESTING OF TOTAL AC SYSTEM AND PACKAGE UNITS:
Unit capacity in tons Refrigeration, shall be computed from the temperature readings and air-flow measurements. Flow measurements shall be preferably by a hot-wire anemometer or a velometer. Computed results shall conform to the specified capacities and the power consumption shall conform to the figures furnished by the manufacturer. Further, Bidder shall furnish all supporting calculations and method of testing likely to be conducted for the performance and capacity tests for the Package Units at manufacturing premises as per standards & procedures being adopted at the time of submitting the tender with complete facilities available for type test required to be witnessed by the clients Engineer and Consultants to give clearance of Package units after satisfactory and successful completion of tests atleast on one each type of units offered for the project. Further Bidder shall also adhere and prove the installation performance at site to meet the required design parameters for the entire system. Methodology likely to be adopted also to be furnished by the Bidder at installation certification stage only this will eligible for final clearance of payment against performance of the AC system which forms the part of the scope of work. Bidder shall also to furnish similar type tests normally conducted by them to establish as a proof of standardization along with the bid documents at the first stage for which will be a mile stone for facilities infrastructure and certification of the capacity.
SPECIAL INSTRUCTION TO THE BIDDER
Unit capacity in tons Refrigeration, shall be computed from the temperature readings and air-flow measurements. Flow measurements shall be preferably by a hot-wire anemometer or a velometer. Computed results shall conform to the specified capacities and the power consumption shall conform to the figures furnished by the manufacturer. Further, Bidder shall furnish all supporting calculations and method of testing likely to be conducted for the performance and capacity tests for the Package Units at manufacturing premises as per standards & procedures being adopted at the time of submitting the tender with complete facilities available for type test required to be witnessed by the clients Engineer and Consultants to give clearance of Package units after satisfactory and successful completion of tests atleast on one each type of units offered for the project. Further Bidder shall also adhere and prove the installation performance at site to meet the required design parameters for the entire system. Methodology likely to be adopted also to be furnished by the Bidder at installation certification stage only this will eligible for final clearance of payment against performance of the AC system which forms the part of the scope of work. Bidder shall also to furnish similar type tests normally conducted by them to establish as a proof of standardization along with the bid documents at the first stage for which will be a mile stone for facilities infrastructure and certification of the capacity.
Mode of measurement for payment of ducting and piping & their insulation shall be as follows::
1 | Ducting
The rate per Sq.meter of the external surface shall include all wastage flanges, gaskets for joints, bolts and nuts, duct supports and hanyer vibration isolation pads or suspenders, flexible connections, inspection doors, dampers, running vanes, straight vanes, and any item which will be required to complete the external insulation and acoustic lining.
The external area shall be calculated by measuring the over all width and depth (including the corner joints) in the centre of the duct section from flange face to flange face in case of ducts length with uniform cross section Total area will be arrived at by adding up the area of all duct sections
In case of taper pieces average width and depth will be worked out as follows
W 1 = Width of small cross section W 2 - Width of large cross section D 1 = Depth of small cross section D 2 = Depth of large cross section
Average Width = W 1 + W 2
2 Average Depth = D 1 + D 2
Width and depth in the case of taper pieces shall be measured at the edge of the collar of the flange for duct sections flatted with angle iron flanges, otherwise at the bottom of the flange where the flanges are of duct sheet.
For circular pieces the diameter of the section midway between large and small diameters shall be measured and adopted as the mean diameter for calculating the surface area of the taper piece. Duct measurements for calculation of area shall be taken before applications of insulation
For the special pieces like bends, branches and tee etc, same principles of areas measurements as for liner and outer periphery along the curvature angle of the piece shall apply
2.0 | DUCT INSULATION/ACOUSTIC LINING:
This item is provided separately for various thickness and shall be paid for an area basis of uninsulated duct The area of the duct to be insulated shall be measured before
G | LIST OF APPROVED MAKES:
The tenderer shall quote his rates on the basis of the price of the brand/make stipulated in the item of works as described in BOQ, specifications and furnished in Technical data. The owner reserves the right to select any of the brands indicated in the "List of Approved Makes" incase of delay in delivery of ordered 'make of item' The contractor cannot claim anything extra if the owner changes the make but within the list of approved make.
Sl | ITEM Acceptable makes
1 | MACHINES
1.1 | Air Cooled Package Units (Floor mounting free standing factory tested units) BlueStar,Batliboi,LG,CarrierAircon,ETA,Voltas,Hitachi(Amtrix) or approved equivalent
2.0. | VENTILATION / EXHAUST FAN
2.1 | Propeller Fans Nicotra,Caryaire,Kanalflakt
2.2 | Inline, Centrifugal Fans -do-
3.0 | DUCTING & ACCESSORIES:
3.1 | G.I. Sheets Tata,HSL,SAIL
3.2 | Aluminium Grilles, Diffusers, Linear Grilles Caryaire,Mapro,Ravistar,AirMaster,Airtech,
3.3 | MS Grilles, Diffusers Tarus,Mapro,RCS,Ravistar,AirMarster,Airtech
4.0 | VALVES
4.1 | Refrigerant Valves Brassomatic,Sant
4.2 | Y' Strainers Sant,DS Ennineering,Emerald
5 | Temp/ Pressure Gauges Taylor,Fiebig,H Guru
6 | Fire Dampers Carairire,Conaire,Ravistar,Airtech
7 | Vibration Isolators Resistoflex,Dunlop,Kanwal
8 | INSULATION
S 1 | Glass wool UP Twiga, Iowens Coming,Kiimco
8.2 | Expanded Polystyrene (TF Quality) Beardsell,Lioyd Insulation
9 | Air Filters Aerosal,Purolator,Thermadune
10 | V belts/Pulleys Fenner,Dunlop
11 | Electric Motors Siemens,Kirlosker,Crompton,ABB
12 | Air Curtains Sidwal,Thermoking
RECOMMENDED MAKES OF MATERIALS (ELECTRICAL)
la. Light Switches/Sockets/Fan Regulators
(Modular type) : MK India/NW/MDS/Anchor/Equivalent
1b. Light Switches/Sockets/
Fan Regulators(Normal) : Anchor/NW/MK/Anchor/Equivalent
2. Ceiling roses : Anchor/MK/Rider/Equivalent
3. Buzzers : Anchor/NW/MDSEquivalent
4 MCBs/MCB Distribution boards/ELCBs : MDS/Schnider/L&T-Hager/
Equivalent
5. Change Over MCBs : Schnider/L&T-Hager/Equivalent
6. LV/HT Cables : CCI/Polycab/Gloster/
universal/Torrent
7. LV Switchgear : Siemens/GEC/L&T/ Schneider
8. Telephone Cables/LAN : Finolex/ Dehon/Mazda
9. TV /CC Cable : Finolex/Pilot/ Equivalent
10. Transformer : KIRLOSKAR/VE/ETE/equivalent
11. PVC conduits : Sudhakar/Precission/Equivalent
12. MS Conduits : Guptha Brand(GB)/Bharath/Equivalent
13. Copper Conductor wires : Finolex/L&T/Polycab/Equivalent
14. Metal clad Sockets : BCH/Crompton/MDS/L&T/Equivalent
15. Cable Glands : HMI/Comet/Equivalent
16. Cable Lugs : Dowel/Jainson Equivalent
17. Water level Controller : Minilec/L&T/Equivalent
18. Indicating Meters : AE/Risliab/IMP/Equivalent
19. Energy meters : BHEL/SIMCO/L&T
: Havell’s/Equivalent
20. Indication Lamps : L&T/C&S/Equivalent
21. Push Buttons : L&T/C&S/Equivalent
22. GI Pipes : Zindal/Tata/Equivalent
23. Street Light Poles : National Tubing Co.
: Bombay poles/Equivalent
24. Light fittings : Philips/ Crompton/ Wipro/Equivalent
25. AB Switches / HG Fuses : Versatek/Hema/Equivalent
26. LAS : LANCO/OBLEM/Equivalent
27. HT Insulators : OBLEM/JAYA/ Equivalent
28. MCCB : L&T/GEC/SEIMENS/Equivalent
29. C. T. : KAPPA/AE/Equivalent
30. Ceiling fans/Exhaust fans : CROMPTON/GEC/USHA/Equivalent
31. CAPACITORS : DUCATI/L&T/ASIAN/Equivalent
32. HT SFU MEGAWIN/ SYSTEM CONTROL/EQUIVALANT
Note:HVAC Contractor has to procure the items and items of work for electrical related system as per the above makes and specifications standardization to be attached along with their bids.
VOLUME-II (BILLS OF QUANTITIES)
BILL OF QUANTITIES FOR HVAC SYSTEM (PACKAGED AC SYSTEM):REF Drgs 1)1-RS-1637 Rev-00 2) 1-RS-1638 Rev-00 3) 1-RS-1639 Rev-00
Sr. No. | Description | Unit | Qty | Rate | Amount
A | EQUIPMENT
1 | AIR COOLED PACKAGE UNITS
Supply, installation, testing & commissioning of Air Cooled package AC.s consisting of indoor & out door units.The indoorunits shall be provided with vibration isolation pads.The out door unit shall be rigidly mounted on a steel base frame grouted to masonary through ribbed rubber with additional supports if necessary.The units shall include blowers,cooling coil,drain pan,washable prefilters,semi hermetic/scroll compressors,condenser coils,adequately sized fans with motors,drier with by pass arrangements,sight glass, electrical panel with controls duly wired,refrigerant &oil duly charged etc. enclosed in attractive sheet metelcabinets with steel base frames , complete as per specifications. Note: Blower should be with High static blower to distribute the cooling air. Motor shall be suitable for 415+ -5% volts 50 cycles, 3 phase AC supply of the following.
a) | Cooling Capacity 15.0 TR/16.5TR with scroll / semi hermitic compressor | Nos | 8
b) | Inter connected copper refrigerant piping for liquid & hot gas lines along with inter connected with 4 C Copper cabling / earthing between outdoor & indoor unit & non return duct dampers. | Sets | 8
c) | Stand by option for 2 Nos. | Sets | 2
d) | Inter connected copper refrigerant piping for liquid and hard gas lines along with inter connected with 4 C Copper cabling / earthing between outdoor and indoor unit and non return duct dampers. | Sets | 2
2 | EXHAUST AND FRESH AIR SYSTEM
Supply, installation, testing and commissioning of centrifugal type exhaust air fan complete fan sections with inlet louvers, dapmers, birdscreen, comprising of pleanum box etc., with all accessories and supporting arrangements . The fan shall be suitable for single Phase , 220 Volt, 50 HZ A.C supply. The fan shall be of following capacity:
a. | Exhaust Air centrifugal fan with inbuilt fan sections.
Capacity (CFM) - 5000
SP mm - 30
| Motor HP - 2 | Sets | 2
b. | Fresh air centrifugal fan with inbuilt fan sections.
Capacity (CFM) - 5000
SP mm - 30
| Motor HP - 2 | Sets | 2
3 | INLINE BOOSTER FANS
a. | Supply, installation testing and commissioning of booster fans with suitable motor and terminal connections for exhaust the quantity of air with all necessary accessories complete. of the capacity, if required for balancing.
| 500 CFM | Nos | R/O
4 | SHEET METAL DUCT :
Supplying, fabricating , installation, testing and commissioning of sheet metal ducts of following thickness including necessary supports , hangers, nut bolts, gasket splitter damper vanes etc. complete as per specifications in accordance with the approved shop drawings and required by the specifications.
a. | 24 G galvanized sheet | Sqm | 410
b. | 22 G galvanized sheet | Sqm | 300
c. | 20 G galvanized sheet | Sqm | 120
d. | 18 G galvanized sheet | Sqm | 20
5 | COLLECTIVE/FILTER PLENUMS
a. | Supplying, fabricating , installation, testing and commissioning of double skin sheet metal plenum and provision for housing in 2 stages (5 & 10 microns) complete with housing frames, access doors, supporting arrangements and including necessary hangers, nut bolts, gasket splitter damper vanes etc. complete as per specifications in accordance with the approved shop drawings and as required by the specifications. | Sqm | 80
6 | FILTERS
Supply, providing and commissioning of fine filters along with filter box with in the plenum box and necessary fixing arrangements
a. | PLEANUM MOUNTED FINE FILTERS 10 MICRONS (2000 CFM / 500 FPM)
i) | Size: 610 X 610 X 150 | Nos | 20
b. | PLENUM FILTERS FLANGE TYPE - 5 MICRONS (2000 CFM / 500 FPM)
i) | Size: 610 X 610 X 300 | Nos | 20
7 | FLEXIBLE CONNECTION
| Supplying, fabricating, installation of double canvas flexible connection constructed of fire resistant material as per the drawings and specifications at a PA unit outlets and branch duct entry if required to limit vibration to structural. | Sqm | 10
8 | DAMPERS:
8.1 | VOLUME CONTROL DAMPERS FOR DUCTS
| Supplying, installing, testing of GI volume control damper within the ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system. | Sqm | 10
8.2 | ACTUATOR DAMPERS
| Supplying, installing, testing of GI volume control damper within the ducts to be provided with suitable links, levers and quadrants for automatic control of volume of air flow and for proper balancing compatible with BMS of the air distribution system at full flow, half flow and close monitoring as required. | Sqm | R/O
8.3 | FIRE DAMPERS (combination fire smoke damper application) :
| Supplying, installation, testing and commissioning of shutter type fire dampers of at least 90 minutes rating ( combination fire smoke damper application as per UL Standard 555 - 1955 specifications & duly approved by CBRI Roorkey) shop drawings complete with control wiring , solenide operated / link and provision to shut off AHU blowers when the damper closes. Dampers shall be located in supply air ducts & return air passage (Fire alarm system Compatible). | Sqm | 10
8.4 | FRESH AIR INLET DAMPER
| Supplying, installing, testing of fresh air inlet damper with 10 micron filter for fresh air with suitable links, levers and quadrants for automatic control of volume of air flow and for proper balancing of the air distribution system. | Lot | 1
9 | SUPPLY/ RETWIN AIR GRILLE:
Supplying, installing, testing and balancing of supply / Retwin air grills of various sizes. Each grill shall be provided with individually adjustable air distribution patterns, grid for straightening the airflow through the collar and register and removable key-operated volume control dampers.
a. | Anodized aluminium perforated grilles with volume control dampers | Sqm | 10
b. | Supplying, installing and testing of return air grilles without any volume control dampers and as per shop drawings.
a. | Anodized aluminium grilles | Sqm | 15
9.1 | SUPPLY AIR DIFFUSER
Supplying, installing, testing and balancing of supply air diffusers of various sizes. Each diffuser shall be equipped with fixed air distribution grid, removable key-operated volume control damper and antismudge ring where required as per approved shop drawings.
a. | M.S. coated diffusers | Sqm | 2
b. | Anodized aluminium grilles | Sqm | 2
9.2 | RETURN AIR DIFFUSER
Supplying, installing, testing and balancing of supply air diffusers of various sizes similar to supply air diffuser without any volume control damper as per approved shop drawings.
a. | M.S. coated diffusers | Sqm | 1
b. | Anodized aluminium grilles | Sqm | 1
10 | LOUVERS:
10.1 | FRESH AIR LOUVERS:
| Supplying, installing & testing of exhaust air GI outlet louvers with bird screen. | Sqm | 2
10.2 | EXHAUST AIR LOUVERS:
| Supplying, installing & testing of exhaust air GI outlet louvers with filter section. | Sqm | 2
11 | INSULATION
11.1 | ACOUSTIC LINING(DUCTS):
Supply, installation of acoustic lining within Supply air ducts with 25mm thick Fibre glass + R.P. Tissue covered with 28G Aluminium Perforated sheet
| 25 mm thick acoustic lining | Sqm | 100
11.2 | THERMAL INSULATION:
Supply, installation external thermal insulation of ducts with factory laminated foil faced Fibre resin bonded glass with vapour barrier & aluminium tape ceiling with necessary over laps as per approved drawings and specifications
a. | 25 mm thick | Sqm | 100
b. | 50 mm thick | Sqm | 300
12 | CONDENSATE DRAIN PIPES FOR PAC S:
Supply, laying , fixing , testing and commissioning of GI pipes complete with all necessary fittings such as elbows, tees, reducers, serviceable traps etc and supports such as clamps etc duly insulated complete as per specifications & drawings.
i) | 50 mm dia | Rmt | 40
ii) | 40 mm dia | Rmt | 40
13 | ELECTRICAL
M.V. SWITCH BOARDS FOR A.C. WORKS(A.C. PACKAGE UNITS)
Supply and installation fof florr mounted powder coated cubical type extendable M.V. switch board with 16 SWG CRCA sheet , 630 Amps rating 3 Ph , and nuetral with Aluminium Bus bars suitable for operation on 415 Volts, 50 Hz, AC supply and incorporating the following features .
I) | Suitable for 10 Nos Package A.C. units | No | 1
ii) | Bus bars (Air insulated) one set of 630 Amps rating 3ph and nuetral Al. bus bars of suitable cross section.
iii) | Incoming TPN moulded case Circuit breaker of approved make with mechanical and electrical inter locking suitable for 630 Amps rating, 50 KV, suitablel thermal release range.
iv) | Outgoing 100A. TP&N Fuse switch units with 63/100 A HRC fuses for(Packaged A.C. units) with 1No Ammeter 0-100A,(Direct),4 Nos indication lamps with fuses, for ON indication of blower, condenser fan & compresers of each package unit. | No | 10
v) | Outgoing 250 A TPN SFU A.C. 23 duty with 250 A HRC fuses for heater package switch Board. | No | 1
vi) | Outgoing 16A TPN MCB for fresh air fan with DOL starter. | No | 3
vii) | Outgoing16A TPN MCB for Exhaust air fan with DOL starter | No | 3
viii) | Cable chamber for all incomimg and ougoing crcuit cables including proper supports and clip on terminals, clamping arrangements etc. | Set | 1
ix) | 1No.Digitol Energy Meter, 1No. Voltmetre and 1No.Ammetre (0-400A) with Phase selector switches, CT.'s & 3 Nos indicating lamps with fuses on Incoming side. | Set | 1
x) | AUXILLARY CONTACTOR (2 NO + 2 NC ) with wiring for tripping incoming MCCB on fire Alarm safety | No | 1
xi) | AUXILARY CONTACTOR (2 NO + 2 NC) 1 No, 5 A toggle switch and 25 A HRC fuse fitting with 6A HRC fuse including wiring provision for providing supply to Hooter / Ananciator from incoming source | No | 1
xii) | AUXILARY CONTACTORS ( 4 NO + 4 NC) 2 Nos push buttons, 2 Nos indication lamps (RED & GREEN) for tripping of blowers in Packaged A.C. units ( Air-stats) | Set | 1
14 | ELECTRIC STRIP HEATER PACKAGES | Set | 3
Supply and installation of winter heating package and Mansoon Dehumidification package in the pre / reheat path as per requirement.
Suitable for 2 sets of 3 package units & 1 set of 4 package units.
I) | Strip Heater package : ( 9+9+9=27Kw ).each set of heater bank,
shall be comprising of (9+9) KW Heaters will be controlled by 2 Nos Humidistats at different Humidity settings and 1 No. safety thermostat
ii) | 9 KW Heaters will be controlled by 1 No control thermostat
iii) | 1 No Air-flow swith on Plenum for tripping the heater supply when the blower is in OFF condition.
iv) | 1 No. OFF push button with element and 1 No. AUXILARY CONTACTOR for manual tripping of heater including wiring / Toggle switch if required.
15 | M.V SWITCH BOARD FOR HEATER PACKAGES:
Supply and installation of powder coated wall mounted cubicle type 16 SWG, CRCA 3 Ph, Nuetral,MV switch board for Heater packages.Aluminium bus bars suitable for operation on 415 V, 50 Hz, AC supply in corporating the following.
I) | Bus bars: ( Air insulated) : One set of 200 A rating 3 Ph of suitable cross section. | No | 1
ii) | In coming 200 A TP&N MCCB , 50 KA,with suitable thermal release unit | No | 1
iii) | Outgoing 63A MCBs with 3 Nos 63 A HRC fuse fittings fuses for back up 3No.s 63 A contactors, 2 Nos on/off indication lamps for 3sets with HRC fuses & 1 No toggle switch, 1 No Ammetre , 0-100A (Direct) for each 27Kw. Heater package | Set | 3
iv) | 60/ 63A FP MCB with 3 Nos 63A HRC fuse fittins/ HRC fuses back up, 2 Nos 63 A contactor, 2 Nos toggle switches, 2 Nos Humidistata for Pan hudifiers | Set | 3
v) | I Voltmeter, Ammetre,(0-200A) with selector switches, CTs , 3 Nos indication lamps with fuses on incoming supply, danger notice plates etc. | Lot | 1
16 | POWER WIRING
Supply, laying and clamping of 1.1KV grade PVC insulated and PVC sheathed Aluminium condutor Armoured cable conductor confirming to relevent IS standards of following sizes as per requirement including Glands, Terminations by Crimping the ends with copper lugs as standard requirement.
I) | a) 95 Sq mm 4 C cable for Heater package Board | Rmt | 30
ii) | b) 35 Sq mm 4 C cable for PAC units | Rmt | 250
iii) | c) 10 Sq mm 4 C cable for 9Kw. Heater Bank | Rmt | 120
iv) | d) 6 Sq mm 4 C cable for Fresh /Exhaust Fans | Rmt | 60
v) | e) 4 Sq mm 4 C cable for Pan Humidifiers | Rmt | 60
17 | CONTROL WIRING FOR AC SYSTEM
I) | Providing necessary control wiring for various fault diagnostic indication, alarms, safety interlocks, air-stat control etc. using 1.1 KV grade armoured PVC insulated multicore copper conductor of 1.5 Sq mm size, including gland, cable terminations, gland earthing etc... as required.
| a) 2 C | Rmt | 100
| b) 4C | Rmt | 50
| c) 6 C | Rmt | 50
ii) | Supply and fixing of MS fabricated cable tray of the following sizes of angle irons with 2 Nos MS flats of size 20 mm X 3 mm at an interval of 450 mm I.e. suitable supports made of MS rods , with suitable hooks , necessary threading, cutting, welding, painting and fixing bolts & nuts etc, as required.
| a) 40 X 40 X 3 mm width 450 mm | Rmt | 50
| b) 25 X 25 X 3 mm width 150 mm | Rmt | 50
18 | EARTHING
I) | Supply and fixing of 25 mm X 4 mm GI strip 2 Runs on surface of wall / recess of
| wall for body earthing as required | Rmt | 50
ii) | Supply & fixing of 8 SWG GI wire on surface of wall or in recess for loop earthing of various equipments as required. | Rmt | 100
19 | Pan Humidifiers
| Supply, Installation,Testing and commissioning of Pan humidifier Package each comprising of M.S Fabricated Tank, 2No,s 3KW. Immerssion Type Heating elements,Over flow / water levell controller inter connected GI piping with valves, Humidistatic controller with wiring to makeup humidity levels in 3 stages as per design requirements. | set | 3
20 | Supply and fixing of Digital type Thermometer for temp.Indication (4" LED display type) with +/- 0.1% in the condition space | No.s | 2
21 | Supply and fixing of Digital type Humidystat for Humidity Indication (4" LED display type) with +/- 0.1% in the condition space. | No.s | 2
PRICE SUMMARY - HVAC SYSTEM
S.NO | DESCRIPTION | REMARKS
1 | AIR COOLED PACKAGE UNITS
2 | ANCILLARIES
3 | ELECTRICAL FOR AC
TOTAL
PRICE BID
BILL OF QUANTITIES FOR HVAC SYSTEM (PACKAGED AC SYSTEM FOR 02-SUPER BAY CLEAN ROOM):REF Drgs 1)1-RS-1637 Rev-00 2) 1-RS-1638 Rev-00 3) 1-RS-1639 Rev-00
Sr. No. | Description | Unit | Qty | Rate | Amount
A | EQUIPMENT
1 | AIR COOLED PACKAGE UNITS
Supply, installation, testing & commissioning of Air Cooled package AC.s consisting of indoor & out door units.The indoorunits shall be provided with vibration isolation pads.The out door unit shall be rigidly mounted on a steel base frame grouted to masonary through ribbed rubber with additional supports if necessary.The units shall include blowers,cooling coil,drain pan,washable prefilters,semi hermetic/scroll compressors,condenser coils,adequately sized fans with motors,drier with by pass arrangements,sight glass, electrical panel with controls duly wired,refrigerant &oil duly charged etc. enclosed in attractive sheet metelcabinets with steel base frames , complete as per specifications. Note: Blower should be with High static blower to distribute the cooling air. Motor shall be suitable for 415+ -5% volts 50 cycles, 3 phase AC supply of the following.
a) | Cooling Capacity 15.0 TR/16.5TR with scroll / semi hermitic compressor | Nos | 8
b) | Inter connected copper refrigerant piping for liquid & hot gas lines along with inter connected with 4 C Copper cabling / earthing between outdoor & indoor unit & non return duct dampers. | Sets | 8
c) | Stand by option for 2 Nos. | Sets | 2
d) | Inter connected copper refrigerant piping for liquid and hard gas lines along with inter connected with 4 C Copper cabling / earthing between outdoor and indoor unit and non return duct dampers. | Sets | 2
2 | EXHAUST AND FRESH AIR SYSTEM
Supply, installation, testing and commissioning of centrifugal type exhaust air fan complete fan sections with inlet louvers, dapmers, birdscreen, comprising of pleanum box etc., with all accessories and supporting arrangements . The fan shall be suitable for single Phase , 220 Volt, 50 HZ A.C supply. The fan shall be of following capacity:
a. | Exhaust Air centrifugal fan with inbuilt fan sections.
Capacity (CFM) - 5000
SP mm - 30
| Motor HP - 2 | Sets | 2
b. | Fresh air centrifugal fan with inbuilt fan sections.
Capacity (CFM) - 5000
SP mm - 30
| Motor HP - 2 | Sets | 2
3 | INLINE BOOSTER FANS
a. | Supply, installation testing and commissioning of booster fans with suitable motor and terminal connections for exhaust the quantity of air with all necessary accessories complete. of the capacity, if required for balancing.
| 500 CFM | Nos | R/O
B | ANCILLARIES
4 | SHEET METAL DUCT :
Supplying, fabricating , installation, testing and commissioning of sheet metal ducts of following thickness including necessary supports , hangers, nut bolts, gasket splitter damper vanes etc. complete as per specifications in accordance with the approved shop drawings and required by the specifications.
a. | 24 G galvanized sheet | Sqm | 410
b. | 22 G galvanized sheet | Sqm | 300
c. | 20 G galvanized sheet | Sqm | 120
d. | 18 G galvanized sheet | Sqm | 20
5 | COLLECTIVE/FILTER PLENUMS
a. | Supplying, fabricating , installation, testing and commissioning of double skin sheet metal plenum and provision for housing in 2 stages (5 & 10 microns) complete with housing frames, access doors, supporting arrangements and including necessary hangers, nut bolts, gasket splitter damper vanes etc. complete as per specifications in accordance with the approved shop drawings and as required by the specifications. | Sqm | 80
6 | FILTERS
Supply, providing and commissioning of fine filters along with filter box with in the plenum box and necessary fixing arrangements
a. | PLEANUM MOUNTED FINE FILTERS 10 MICRONS (2000 CFM / 500 FPM)
i) | Size: 610 X 610 X 150 | Nos | 20
b. | PLENUM FILTERS FLANGE TYPE - 5 MICRONS (2000 CFM / 500 FPM)
i) | Size: 610 X 610 X 300 | Nos | 20
7 | FLEXIBLE CONNECTION
| Supplying, fabricating, installation of double canvas flexible connection constructed of fire resistant material as per the drawings and specifications at a PA unit outlets and branch duct entry if required to limit vibration to structural. | Sqm | 10
8 | DAMPERS:
8.1 | VOLUME CONTROL DAMPERS FOR DUCTS
| Supplying, installing, testing of GI volume control damper within the ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system. | Sqm | 10
8.2 | ACTUATOR DAMPERS
| Supplying, installing, testing of GI volume control damper within the ducts to be provided with suitable links, levers and quadrants for automatic control of volume of air flow and for proper balancing compatible with BMS of the air distribution system at full flow, half flow and close monitoring as required. | Sqm | R/O
8.3 | FIRE DAMPERS (combination fire smoke damper application) :
| Supplying, installation, testing and commissioning of shutter type fire dampers of at least 90 minutes rating ( combination fire smoke damper application as per UL Standard 555 - 1955 specifications & duly approved by CBRI Roorkey) shop drawings complete with control wiring , solenide operated / link and provision to shut off AHU blowers when the damper closes. Dampers shall be located in supply air ducts & return air passage (Fire alarm system Compatible). | Sqm | 10
8.4 | FRESH AIR INLET DAMPER
| Supplying, installing, testing of fresh air inlet damper with 10 micron filter for fresh air with suitable links, levers and quadrants for automatic control of volume of air flow and for proper balancing of the air distribution system. | Lot | 1
9 | SUPPLY/ RETWIN AIR GRILLE:
Supplying, installing, testing and balancing of supply / Retwin air grills of various sizes. Each grill shall be provided with individually adjustable air distribution patterns, grid for straightening the airflow through the collar and register and removable key-operated volume control dampers.
a. | Anodized aluminium perforated grilles with volume control dampers | Sqm | 10
b. | Supplying, installing and testing of return air grilles without any volume control dampers and as per shop drawings.
a. | Anodized aluminium grilles | Sqm | 15
9.1 | SUPPLY AIR DIFFUSER
Supplying, installing, testing and balancing of supply air diffusers of various sizes. Each diffuser shall be equipped with fixed air distribution grid, removable key-operated volume control damper and antismudge ring where required as per approved shop drawings.
a. | M.S. coated diffusers | Sqm | 2
b. | Anodized aluminium grilles | Sqm | 2
9.2 | RETURN AIR DIFFUSER
Supplying, installing, testing and balancing of supply air diffusers of various sizes similar to supply air diffuser without any volume control damper as per approved shop drawings.
a. | M.S. coated diffusers | Sqm | 1
b. | Anodized aluminium grilles | Sqm | 1
10 | LOUVERS:
10.1 | FRESH AIR LOUVERS:
| Supplying, installing & testing of exhaust air GI outlet louvers with bird screen. | Sqm | 2
10.2 | EXHAUST AIR LOUVERS:
| Supplying, installing & testing of exhaust air GI outlet louvers with filter section. | Sqm | 2
11 | INSULATION
11.1 | ACOUSTIC LINING(DUCTS):
Supply, installation of acoustic lining within Supply air ducts with 25mm thick Fibre glass + R.P. Tissue covered with 28G Aluminium Perforated sheet
| 25 mm thick acoustic lining | Sqm | 100
11.2 | THERMAL INSULATION:
Supply, installation external thermal insulation of ducts with factory laminated foil faced Fibre resin bonded glass with vapour barrier & aluminium tape ceiling with necessary over laps as per approved drawings and specifications
a. | 25 mm thick | Sqm | 100
b. | 50 mm thick | Sqm | 300
12 | CONDENSATE DRAIN PIPES FOR PAC S:
Supply, laying , fixing , testing and commissioning of GI pipes complete with all necessary fittings such as elbows, tees, reducers, serviceable traps etc and supports such as clamps etc duly insulated complete as per specifications & drawings.
i) | 50 mm dia | Rmt | 40
ii) | 40 mm dia | Rmt | 40
13 | ELECTRICAL
M.V. SWITCH BOARDS FOR A.C. WORKS(A.C. PACKAGE UNITS)
Supply and installation fof florr mounted powder coated cubical type extendable M.V. switch board with 16 SWG CRCA sheet , 630 Amps rating 3 Ph , and nuetral with Aluminium Bus bars suitable for operation on 415 Volts, 50 Hz, AC supply and incorporating the following features .
I) | Suitable for 10 Nos Package A.C. units | No | 1
ii) | Bus bars (Air insulated) one set of 630 Amps rating 3ph and nuetral Al. bus bars of suitable cross section.
iii) | Incoming TPN moulded case Circuit breaker of approved make with mechanical and electrical inter locking suitable for 630 Amps rating, 50 KV, suitablel thermal release range.
iv) | Outgoing 100A. TP&N Fuse switch units with 63/100 A HRC fuses for(Packaged A.C. units) with 1No Ammeter 0-100A,(Direct),4 Nos indication lamps with fuses, for ON indication of blower, condenser fan & compresers of each package unit. | No | 10
v) | Outgoing 250 A TPN SFU A.C. 23 duty with 250 A HRC fuses for heater package switch Board. | No | 1
vi) | Outgoing 16A TPN MCB for fresh air fan with DOL starter. | No | 3
vii) | Outgoing16A TPN MCB for Exhaust air fan with DOL starter | No | 3
viii) | Cable chamber for all incomimg and ougoing crcuit cables including proper supports and clip on terminals, clamping arrangements etc. | Set | 1
ix) | 1No.Digitol Energy Meter, 1No. Voltmetre and 1No.Ammetre (0-400A) with Phase selector switches, CT.'s & 3 Nos indicating lamps with fuses on Incoming side. | Set | 1
x) | AUXILLARY CONTACTOR (2 NO + 2 NC ) with wiring for tripping incoming MCCB on fire Alarm safety | No | 1
xi) | AUXILARY CONTACTOR (2 NO + 2 NC) 1 No, 5 A toggle switch and 25 A HRC fuse fitting with 6A HRC fuse including wiring provision for providing supply to Hooter / Ananciator from incoming source | No | 1
xii) | AUXILARY CONTACTORS ( 4 NO + 4 NC) 2 Nos push buttons, 2 Nos indication lamps (RED & GREEN) for tripping of blowers in Packaged A.C. units ( Air-stats) | Set | 1
14 | ELECTRIC STRIP HEATER PACKAGES | Set | 3
Supply and installation of winter heating package and Mansoon Dehumidification package in the pre / reheat path as per requirement.
Suitable for 2 sets of 3 package units & 1 set of 4 package units.
I) | Strip Heater package : ( 9+9+9=27Kw ).each set of heater bank,
shall be comprising of (9+9) KW Heaters will be controlled by 2 Nos Humidistats at different Humidity settings and 1 No. safety thermostat
ii) | 9 KW Heaters will be controlled by 1 No control thermostat
iii) | 1 No Air-flow swith on Plenum for tripping the heater supply when the blower is in OFF condition.
iv) | 1 No. OFF push button with element and 1 No. AUXILARY CONTACTOR for manual tripping of heater including wiring / Toggle switch if required.
15 | M.V SWITCH BOARD FOR HEATER PACKAGES:
Supply and installation of powder coated wall mounted cubicle type 16 SWG, CRCA 3 Ph, Nuetral,MV switch board for Heater packages.Aluminium bus bars suitable for operation on 415 V, 50 Hz, AC supply in corporating the following.
I) | Bus bars: ( Air insulated) : One set of 200 A rating 3 Ph of suitable cross section. | No | 1
ii) | In coming 200 A TP&N MCCB , 50 KA,with suitable thermal release unit | No | 1
iii) | Outgoing 63A MCBs with 3 Nos 63 A HRC fuse fittings fuses for back up 3No.s 63 A contactors, 2 Nos on/off indication lamps for 3sets with HRC fuses & 1 No toggle switch, 1 No Ammetre , 0-100A (Direct) for each 27Kw. Heater package | Set | 3
iv) | 60/ 63A FP MCB with 3 Nos 63A HRC fuse fittins/ HRC fuses back up, 2 Nos 63 A contactor, 2 Nos toggle switches, 2 Nos Humidistata for Pan hudifiers | Set | 3
v) | I Voltmeter, Ammetre,(0-200A) with selector switches, CTs , 3 Nos indication lamps with fuses on incoming supply, danger notice plates etc. | Lot | 1
16 | POWER WIRING
Supply, laying and clamping of 1.1KV grade PVC insulated and PVC sheathed Aluminium condutor Armoured cable conductor confirming to relevent IS standards of following sizes as per requirement including Glands, Terminations by Crimping the ends with copper lugs as standard requirement.
I) | a) 95 Sq mm 4 C cable for Heater package Board | Rmt | 30
ii) | b) 35 Sq mm 4 C cable for PAC units | Rmt | 250
iii) | c) 10 Sq mm 4 C cable for 9Kw. Heater Bank | Rmt | 120
iv) | d) 6 Sq mm 4 C cable for Fresh /Exhaust Fans | Rmt | 60
v) | e) 4 Sq mm 4 C cable for Pan Humidifiers | Rmt | 60
17 | CONTROL WIRING FOR AC SYSTEM
I) | Providing necessary control wiring for various fault diagnostic indication, alarms, safety interlocks, air-stat control etc. using 1.1 KV grade armoured PVC insulated multicore copper conductor of 1.5 Sq mm size, including gland, cable terminations, gland earthing etc... as required.
| a) 2 C | Rmt | 100
| b) 4C | Rmt | 50
| c) 6 C | Rmt | 50
ii) | Supply and fixing of MS fabricated cable tray of the following sizes of angle irons with 2 Nos MS flats of size 20 mm X 3 mm at an interval of 450 mm I.e. suitable supports made of MS rods , with suitable hooks , necessary threading, cutting, welding, painting and fixing bolts & nuts etc, as required.
| a) 40 X 40 X 3 mm width 450 mm | Rmt | 50
| b) 25 X 25 X 3 mm width 150 mm | Rmt | 50
18 | EARTHING
I) | Supply and fixing of 25 mm X 4 mm GI strip 2 Runs on surface of wall / recess of
| wall for body earthing as required | Rmt | 50
ii) | Supply & fixing of 8 SWG GI wire on surface of wall or in recess for loop earthing of various equipments as required. | Rmt | 100
19 | Pan Humidifiers
| Supply, Installation,Testing and commissioning of Pan humidifier Package each comprising of M.S Fabricated Tank, 2No,s 3KW. Immerssion Type Heating elements,Over flow / water levell controller inter connected GI piping with valves, Humidistatic controller with wiring to makeup humidity levels in 3 stages as per design requirements. | set | 3
20 | Supply and fixing of Digital type Thermometer for temp.Indication (4" LED display type) with +/- 0.1% in the condition space | No.s | 2
21 | Supply and fixing of Digital type Humidystat for Humidity Indication (4" LED display type) with +/- 0.1% in the condition space. | No.s | 2
TOTAL
PRICE SUMMARY - HVAC SYSTEM
S.NO | DESCRIPTION | AMOUNT
1 | AIR COOLED PACKAGE UNITS
2 | ANCILLARIES
3 | ELECTRICAL FOR AC
TOTAL