## DGP
BOQ for Erection Testing & Commissioning (ETC) Works (Rev 00)
Project : Substation Package-SS02 for Extension of I) 400kV Biharshariff S/s, II) 400kV Jamshedpur S/s, III) 400 kV Gazuwaka S/s, IV) 400 kV Rengali S/s, V) 400 kV Rourkela S/s, VI) 400 kV Durgapur S/s & VII) 400 kV Gorakhpur S/s associated with Eastern Region Strengthening Scheme-IX
Customer : Power Grid Corporation of India Limited
Location : 400kV Durgapur S/s
S.No. | Voltage Class (kV) | Type | Description | Unit | Qty. | Unit Rate (Rs.) | Amount (Rs.)
MAIN EQUIPMENTS
1.1 | 400 kV | Outdoor | ETC of 125MVAr, 3-Ph (BHEL Make) Reactor complete in all respects alongwith Marshalling Kiosk, terminal connectors, accessories, with oil. Work includes erection of all auxiliaries, viz turrets, bushings, terminal connectors, filling of oil, oil filteration, Oil testing, laying of cable from Reactor auxiliaries to MK etc as required to complete the installation of 125MVAr reactor | Nos. | 2 |  | 0
1.2 | 400 kV | Outdoor | Dragging charges of above mentioned Reactor (1 No.) upto plinth | m | 100 |  | 0
2.1 | 400 kV | With/Without PIR & with CSD | ETC of SF6, 3 Phase Circuit Breaker with Controlled Switching Device alongwith lattice type GS supporting structure, terminal connectors, Breaker Control Cabinets, ladder and interpole cabling. Work also includes mounting of CSD in respective Relay Panel in Control Room (Supervision of Erection, Testing and commissioning will be done by supplier. Supplier will bring Timing kit and Gas leak detector only. Necessary manpower support, tools, tackles and testing kit to be in scope of ETC contractor). | Nos. | 1 |  | 0
2.2 | 400 kV | CSD | Laying of Special cable (for Control Switching Device) between existing/new SF6, 3 Ph Circuit Breaker (in Yard) and Relay Panel (in Control Room) | m | 1350 |  | 0
3 | 400 kV | HDB (Normal) | 3 Ph, Isolator, motor/ manual operated complete with 9 nos. of support insulators & terminal connectors and interpole cabling without support structure |  |  |  | 0
3.1 |  |  | - with one earth switch (motor/ manual operated) | Nos. | 3 |  | 0
4 | 400 kV | Upto 3000 A | 1 Ph, Current Transformer (3000 A) , live/dead tank complete with terminal connectors without support structure. | Nos. | 3 |  | 0
5 | 336 kV |  | 1 Phase, Gapless type Metal Oxide Surge Arrester complete with surge counter, leakage current meter, insulating base, connecting cable and terminal connectors without support structure. | Nos. | 6 |  | 0
6 | 400 kV | Solidcore wirh corona ring | Post Insulators complete with corona ring & terminal connectors without support structure. | Nos. | 6 |  | 0
7 | ILLUMINATION SYSTEM (Only Unloading, Storage is in scope of ETC Contractor) | [5 empty] | 0
7.1 | - | Illumination Sys | Lighting Panels, fixtures, Receptacles and other accessories/materials etc. as required for complete installation and commissioning of Illumination System (Refer Annexure-B for details) | Lot | 1 |  | 0
8 | BUS BAR MATERIALS | [5 empty] | 0
8.1 | Stringing hardware | [5 empty] | 0
8.1.1 | 400 kV | Double Tension | Dismantling of existing Tension insulator string with double/single anchoring point , string comprising 2X25 nos. Disc with hardware set with all accessories including tension clamp with/ without Turn Buckle set suitable for twin/quad conductor. | Set | 6 |  | 0
8.1.2 | 400 kV | Double Tension | Tension insulator string with double/single anchoring point , string comprising 2X25 nos. Disc with hardware set with all accessories including tension clamp with/ without Turn Buckle set suitable for twin/quad conductor. | Set | 6 |  | 0
8.1.3 | 400 kV | Single Suspension | Suspension insulator string comprising 1X25 nos. disc with hardware set with all accessories including drop/through type suspension clamp suitable for twin/quad conductor. | Set | 9 |  | 0
8.2 | - | ACSR Moose/ Zebra | Dismantling of exisitng conductor complete with Tee connectors for droppers to equipment connections, PG clamps for busbar jumpering, Twin/Quad bundle spacers etc to complete. | Km | 0.2 |  | 0
8.3 | - | ACSR Moose/ Zebra | Conductor complete with Tee connectors for droppers to equipment connections, PG clamps for busbar jumpering, Twin/Quad bundle spacers etc to complete. | Km | 0.9 |  | 0
8.4 |  | 4.5"/ 4.0" | Al Tube (ETC of 4" Al.Tube includes Aluminium welding and bending to be included. Welding sleeve tube will be supplied by BHEL) | m | 50 |  | 0
8.5 | - | 7/9 SWG OR 7/8SWG | GI Stranded Shield wire including tension clamp, PG clamp and clamping on structure for down conductor, fixing/bolting with earth strip etc to complete. | Km | 0.3 |  | 0
| ENGINEERED ITEMS | [5 empty] | 0
9 |  |  | Cabling including laying, tagging , dressing, ferruling, lugging, ,soldering, tapping, jointing, crimping, termination, and drilling/ cutting holes in cable gland plates- laying can be either on (existing/new) trays, supports, underground (buried in ground or through GI/PVC pipe), over ground, through wall etc. All erection materials viz. ferrules, copper lugs, cable ties / straps, Al. tags, markers, GI / PVC wall sleeves with rubber / nylon bushes and flexible steel conduits shall be supplied by bidder. Glands shall be quoted seprately. (Removal of Pre-cast trench cover for cable laying & replenishing cover on trench after cable laying in case of existing trench is also in bidder's scope) |  |  |  | 0
9.1 |  |  | Control cables |  |  |  | 0
9.1.1 |  | PVC | 5Cx2.5 sqmm Cu | Km | 5 |  | 0
9.1.2 |  | PVC | 7Cx2.5 sqmm Cu | Km | 0.6 |  | 0
9.1.3 |  | PVC | 10Cx2.5 sqmm Cu | Km | 9.8 |  | 0
9.1.4 |  | PVC | 14Cx2.5 sqmm Cu | Km | 4.4 |  | 0
9.1.5 |  | PVC | 19Cx2.5 sqmm Cu | Km | 3.8 |  | 0
0
9.2 |  |  | Auxiliary Power cables |  |  |  | 0
9.2.1 |  | PVC | 2Cx2.5 sqmm Al/Cu | Km | 1.4 |  | 0
9.2.2 |  | PVC | 2Cx6 sqmm Al/Cu | Km | 0.9 |  | 0
9.2.3 |  | PVC | 4Cx6 sqmm Al/Cu | Km | 0.7 |  | 0
9.2.4 |  | PVC | 4Cx16 sqmm Al/Cu | Km | 0.8 |  | 0
9.2.5 |  | PVC | 3.5Cx35 sqmm Al/Cu | Km | 0.6 |  | 0
9.2.6 |  | PVC | 3.5Cx70 sqmm Al/Cu | Km | 1.1 |  | 0
0
10 |  |  | Tin/ Nickel, Nichel/chromium - Plated (coating thickness not less than 10 microns) brass cable glands, double compression heavy-duty type complete with necessary armour clamp & tapered washer etc for the following cables (Bidder's Scope is to supply and fixing) Qty may vary by ±50% (Cable glands to be procured from Powergrid approved Vendors) |  |  |  | 0
10.1 |  | PVC | 5Cx2.5 sqmm Al/Cu | Nos. | 56 |  | 0
10.2 |  | PVC | 7Cx2.5 sqmm Al/Cu | Nos. | 8 |  | 0
10.3 |  | PVC | 10Cx2.5 sqmm Al/Cu | Nos. | 58 |  | 0
10.4 |  | PVC | 14Cx2.5 sqmm Al/Cu | Nos. | 48 |  | 0
10.5 |  | PVC | 19Cx2.5 sqmm Al/Cu | Nos. | 40 |  | 0
10.6 |  | PVC | 2Cx2.5 sqmm Al/Cu | Nos. | 14 |  | 0
10.7 |  | PVC | 2Cx6 sqmm Al/Cu | Nos. | 38 |  | 0
10.8 |  | PVC | 4Cx6 sqmm Al/Cu | Nos. | 42 |  | 0
10.9 |  | PVC | 4Cx16 sqmm Al/Cu | Nos. | 6 |  | 0
10.1 |  | PVC | 3.5Cx35 sqmm Al/Cu | Nos. | 8 |  | 0
10.11 |  | PVC | 3.5Cx70 sqmm Al/Cu | Nos. | 6 |  | 0
0
11 |  |  | Installation of Cable Sealing System (as per specfication enclosed at Annexure-B) | No. of cable entries | 2 |  | 0
0
12 |  |  | Marshalling Kiosks & CT Junction Boxes |  |  |  | 0
12.1 |  |  | Bay Marshalling Kiosks ( Outdoor, Floor mounted on cable trench) | Nos. | 2 |  | 0
12.2 |  |  | CT Junction Box (on CT structure) | Nos. | 1 |  | 0
0
13 |  |  | Laying of Cable trays: including bends, tees, elbow, reducers, stiffeners coupler plates, bolting to racks, structure etc. to complete. |  |  |  | 0
13.1 |  |  | 150 to 750 mm wide, 2.5 M long Ladder type | m | 100 |  | 0
13.2 |  |  | 100 to 750 mm wide, 2.5 M long Perforated type | m | 100 |  | 0
14 |  |  | Cable Rack work includes welding of mild steel & painted racks (paint suply in scope of bidder) on inserts of trench walls in trenches in switchyard and control room. Cable rack assembly will be of 2/3/4 tier. (supply of MS Angles is in bidder's scope) | MT | 2 |  | 0
15 |  |  | Laying of PVC conduits at a depth of 300mm including excavation, backfilling, making and repairing of walls in trenches, cutting, threading, fixing of sockets/ bends where required etc. complete. Both ends of PVC conduits shall be closed by plastering. (Payment will be made for the as erected pipe length) |  |  |  | 0
15.1 |  |  | PVC pipe, 50/ 63 NB | m | 1755 |  | 0
15.2 |  |  | PVC Pipe, 100/ 110NB | m | 375 |  | 0
16 |  |  | Laying of GI conduits at a depth of 300mm including excavation, backfilling, making and repairing of walls in trenches, cutting, threading, fixing of sockets/ bends where required etc. complete. Both ends of GI conduits shall be closed by plastering. (Payment will be made for the as erected pipe length) |  |  |  | 0
16.1 |  |  | GI pipe, 50/ 63 NB | m | 100 |  | 0
16.2 |  |  | GI Pipe, 100/ 110NB | m | 100 |  | 0
17 |  |  | Earthing material- The earthing includes earthing of all switchyard equipment, towers, pipe structure, cable trenches, fence, pipe electrode for LA, CVT, neutral of transformer & at interconnections of other grids, Control room equipments using necessary Connectors for earthing flats. Earthing clamping shall be carried out by ETC contractor. GS strip including cutting, bending, welding with 40 mm dia MS rod riser/earth strip, applying zinc rich paint, clamping to structure/building wall etc. to complete. Hardware required for connecting flat on pads of structure & equipment included in scope. The Earthing of equipments, Auxiliary Earthmats under Iso/ ES/ CB MOM boxes shall be carried out as per C/ENG/STD/EARTHING (SH-1 to 28) : |  |  |  | 0
17.1 |  |  | 75 x 12 mm GI Flat | km | 0.4 |  | 0
17.2 |  |  | 50 x 6 mm GI Flat | km | 0.35 |  | 0
0
18 |  |  | Galvanised steel Lattice Structures including hardwares for Towers, beams & LM | MT | 21.5 |  | 0
19 |  |  | Galvanised steel Pipe Structures including hardwares for equipment support | MT | 11.5 |  | 0
20 |  |  | LT Switchgear |  |  |  | 0
20.1 |  |  | Extension of existing 415V ACDB (Supply, mounting & wiring under ETC contractor scope) 100 A, 4 pole MCCB module (Type E) - 2 nos 63 A, 4 pole MCCB module (Type E) – 5 nos Specification: Voltage & frequency - 415V ± 10% & 50Hz ± 5% Rated operated duty - As per IS Rated service short-circuit Breaking capacity (Ics) - 20 kA (RMS) Short Circuit making current - 45 kA (Peak) No. of auxiliary Contacts - 1 NO &1 NC Rated Ultimate Short Circuit breaking capacity AC component - 20 kA (RMS) DC component - As per IS 13947 NOTE: 1) The scope includes material required to mount 100A MCCB and 63A MCCB, such as wires, lugs,ferrules, TB's, mounting accessories etc. 2) Make shall be POWERGRID approved | Set | 1 |  | 0
20.2 |  |  | Extension of existing 220V DCDB (Supply, mounting & wiring under ETC contractor scope) 32 A double pole MCB Module – 12 nos. Specification: Voltage - 250V Rated operated duty - As per IS Rated service short-circuit Breaking capacity (Ics) - 4 kA No. of auxiliary Contacts - 1 NO &1 NC Rated Ultimate Short Circuit breaking capacity AC component - As per IS DC component - As per IS 13947 NOTE: 1) The scope includes material required to mount 32A double pin MCB, such as wires, lugs,ferrules, TB's, mounting accessories etc. 2) Make shall be POWERGRID approved | Set | 1 |  | 0
21 |  |  | Control & Relay Panel (Testing and commissioning of relays in scope of panel OEM. Necessary manpower support, tools, tackles and testing equipment to be in scope of ETC contractor) |  |  |  | 0
21.1 |  |  | Circuit Breaker Relay panel without Auto-Reclose (1 set = 1 panel) | Set | 1 |  | 0
21.2 |  |  | Augmentation of Existing control panel (Loose fitments) Refer Note 1 | Sets | 2 |  | 0
21.3 |  |  | Reactor Protection Panel (1 set = 1 panel) | Sets | 2 |  | 0
21.4 |  |  | Common Equipments-special relay test kit (Only unloading, Storage in ETC contractor scope) | Set | 1 |  | 0
21.5 |  |  | BCU for NTAMC System (1 set = 1 panel) | Set | 1 |  | 0
22 |  |  | Repair/Modification work in Control room for fixing of 400 kV panels in present scope including covering of gap and floor finishing. | Lot | 1 |  | 0
23 |  |  | Making Cut out in the floor of existing control room, work includes cutting RCC & finishing | sq. m | 10 |  | 0
24 |  |  | Supplying Rubber mats (Class-A suitable for 1.1 kV as per IS: 15652) and laying in front of Panels | SQ. M | 10 |  | 0
25 |  |  | Panel Supporting Angles / Channel etc on cable trench in Control Room & Bay Control Room, Vertical support for cables etc (Including Supply). | MT | 1 |  | 0
26 |  |  | Dismantling & re-erection of terminal connector wherever equipment installation is not in scope of contractor. Connectors shall be provided by PGCIL/BHEL. Any other ETC work related to equipment is not in the scope of this BOQ. (Eqpmt details: 400kV Isolators (3-ph) - 1 nos) | Nos. of Eqpmts | 1 |  | 0
27 |  |  | Unloading, storage & handing over of Essential/ Mandatory spares/Maintenance equipments to Customer as per Annexure-A | Lot | 1 |  | 0
|  |  | Total Amount (Rs.) |  |  |  | 0
Following also forms the scope of ETC work in addition to above, but not limited to this.
1 | Loading / Unloading, verification, handling, shifting to & from stores, proper storage, assembly, installation, pre-commissioning test and commissioning tests (As per Powergrid/BHEL FQP) are included in the scope. Necessary skilled electrician & labour to be provided by ETC contractor to OEM during testing & commissioning.
2 | All the drawings and documents as per Annexure-1 shall be followed for ETC work.
3 | Annexure- 2 (Powergrid Technical Specification, Section - Switchyard Erection (R8)) shall be followed for ETC work. All pre/commissioning activities and works work for substation equipment shall be carried out in accordance with Powergrid's ''Pre- Commissioning procedures and formats for substation bay equipments" by the contractor.
4 | Minor Civil works such as modification of civil foundations, making holes in the trenches/ control room building, grouting, fixing of trench material will be in the scope of ETC contractor.
5 | Removal of gravel, if gravelling is done, for connection of Equipment earthing strip to the existing mat (wherever earthing mat is already laid), and after completion of earthing , contractor should place the gravel to bring it in original shape.
6 | The quantities given in items mentioned above may undergo a change to any extent.
7 | Quoted rates are deemed to be inclusive of miscellaneous works viz erection of clamps and connectors.
8 | All paint , welding electrodes & other consumable by contract supplies shall be part of ETC works. Paint /welding electrode make etc. is subject to BHEL/CUSTOMER site incharge approval.
9 | Equipment erection (say Isolator ) means complete erection, metallics, post insulator, connectors (expansion/rigid tubular for Al.Tube / single/double/quadraple conductor), connection to the next in line (if connected to overhead busbar or droppers) including PG clamps/Tee connectors etc. This will be clear from the enclosed electrical layout drawings.
10 | Equipment and tower erection would include supply and erection of miscellanneous items , viz Phase colour discs , labels painting of equipments , phase colour painting , phase marking , bay identification board , danger plates , rubber mats , device number marking on the equipment, keyboard etc as per site requirements. Supply & Mounting of phase color discs & Danger plates shall be as per IS-2551; 1982 & IS 5; 1978.
11 | Welding of Aluminium tubes ( supply of welding sleeve excluded) as per Annexure-3 is in ETC contractor's scope and joints shall be tested by radiography. Welding and Bending machines and any other equipment will be in ETC Contractor scope.
12 | Completete ETC package is under the scope of bidder. All TNP including oil filterating machine, cranes etc. required to complete the job shall be provided by bidder only.
13 | Supervision of erection, Testing & commissioning of one no. Isolator of each type shall be done by supplier. Necessary menpower support, tools, tackles etc shall be in the scope of ETC contractor.
14 | Testing instruments (dully calibrated) have to be arranged by ETC Contractor at it's own cost ( List is only provided for information , if any other instrument not mentioned below but required for sucessful completion of ETC work shall be in ETC contractor's scope) , (However OMICRON or equivalent kit for Numerical relay testing shall be arranged by BHEL.)
15 | DCRM (OPERATIONAL ANALYZER )
16 | Contact Resistance Measurement kit (CRM)
17 | Capacitance and Tan delta measurement Kit
17.1 | Dew Point Measurement kit
17.2 | 5kV/1kV Megger
17.3 | Primary current Injection Kit
17.4 | Secondary current/Voltgae Injection kit
17.5 | 1Ph Variac
17.6 | Multimeters
17.7 | Clamp on meter
17.8 | Relay test kit