## Package1
BOQ for Erection Testing & Commissioning (ETC) Works for 765kV switchyard Rev 01
Project : 765kV S/S Banaskantha |  |  |  |  | Package - 1
Customer : POWERGRID CORPORATION OF INDIA LTD.
Note: | This BOQ covers only ETC work for 765 kV Switchyard excluding unloading and storage. Unloading and storage of all the material required for 765kV Switchyard is covered under separate contract. ETC contractor of 765kV switchyard package shall ask in writing to unloading and storage contractor for issuance of items/material required for 765kV Switchyard. All arrangement for Lifting and shifting of 765kV equipments/ items (for 765kV Switchyard) from the storage area shall be in the scope of of the contractor of 765kV Switchyard.Bidder should quote only for ETC work in this BOQ..
S.No. | Voltage Class (kV) | Type | Description | Unit | Main Qty | Extn Qty | Total Qty | Unit Price | Total Price (Rs.)
765kV Equipments
1 | 765kV | 3 Ph | 3 Phase SF6 Circuit Breaker alongwith lattice type Gi supporting structure, terminal connectors, Breaker Control Cabinets, ladder and interpole cabling,SF6 Gas cylinders with controlled switching scheme. (Supervision of Erection, Testing and commissioning will be done by supplier. Supplier will bring Timing kit and Gas leak detector only. Necessary manpower support, tools, tackles and testing kit to be in scope of ETC contractor).
1.1 |  |  | With PIR & with CSD | Sets | 3 | 2 | 5 |  | 0
1.2 |  |  | With PIR & without CSD | Sets | 2 | 2 | 4 |  | 0
1.3 |  |  | Without PIR & with CSD | Sets | 5 | 2 | 7 |  | 0
1.4 |  | CSD | Special cabling between CB and Relay Panel in SPR | m | 600 | 300 | 900 |  | 0
2 | 765kV | 1 Ph | 1 Phase SF6 Circuit Breaker alongwith lattice type Gi supporting structure, terminal connectors, Breaker Control Cabinets, ladder and interpole cabling,SF6 Gas cylinders with controlled switching scheme. (Supervision of Erection, Testing and commissioning will be done by supplier. Supplier will bring Timing kit and Gas leak detector only. Necessary manpower support, tools, tackles and testing kit to be in scope of ETC contractor). | [5 empty] | 0
2.1 |  |  | Without PIR & with CSD | Nos. | 1 |  | 1 |  | 0
0
3 | 765kV | Knee Type | 3 Phase, Knee Type Isolator, motor operated Isolator and earth switch electrically ganged complete with 6 nos. of support insulators & terminal connectors without support structure ( 3 Nos. operating rod insulators are also included) | [5 empty] | 0
3.1 |  |  | - with one earth switch (motor operated) | Nos. | 17 | 12 | 29 |  | 0
3.2 |  |  | - with two earth switch (motor operated) | Nos. | 2 |  | 2 |  | 0
4 | 765kV | Knee Type | 1 Phase, Knee Type Isolator, motor operated Isolator and earth switch electrically ganged complete with 2 nos. of support insulators & terminal connectors without support structure (Operating Rod insulator :1 No.s for Isolator w/o earth switch , 2 Nos. of operating rod insulator for isolator with 1 E/S are also included) | [5 empty] | 0
4.1 |  |  | - without earth switch | Nos. | 12 | 6 | 18 |  | 0
4.2 |  |  | - with one earth switch (motor operated) | Nos. | 33 | 12 | 45 |  | 0
| Note: 624kV LA, 765kV CT or 765kV CVT may or may not be despatched in container by the manufacturers, it will be ETC contractor's responsibilty to unload container and then un load equipments from the container. No additional price for unloading shall be payable. | [7 empty] | 0
5 | 624kV | LA | 1 Phase, Gapless type Metal Oxide Surge Arrester complete with surge counter, leakage current meter, insulating base, connecting cable/strip and terminal connectors. without support structure. | Nos. | 24 | 12 | 36 |  | 0
6 | 765kV |  | 1 Ph, Current Transformer complete with terminal connectors without support structure. | Nos. | 24 | 12 | 36 |  | 0
7 | 765kV |  | 1 Ph, Capacitive Voltage Transformer complete with terminal connectors without support structure. | Nos. | 12 | 6 | 18 |  | 0
8 | 765kV | 8kN | Bus support Insulators (Solid core Post insulator) with corona ring complete with terminal connectors without support structure. | Nos. | 66 | 32 | 98 |  | 0
9 | 765kV | 1mH | Wave Trap pedestal mounted including 3 Nos. 765kV Post Insulators and Terminal connectors without support structure. | Nos. | 4 | 4 | 8 |  | 0
0
| Stringing Work | [7 empty] | 0
0
10 | Stringing hardware | [7 empty] | 0
|  |  | Inclusive of fixing various types of clamps, connectors, spacers, corona rings, sleeves, aluminum welding, fixing of socket and bends, | [5 empty] | 0
10.1 | 765 kV | Double Tension | 765kV Double tension insulator string comprising 2x44 discs with subconductor spacing 450mm suitable for quad AAC Bull conductor with / without turn Buckle | set | 120 | 42 | 162 |  | 0
10.2 | 765 kV | Single Suspension | 765kV Single suspension insulator string comprising 1x44 discs with subconductor spacing 450mm suitable for quad AAC Bull conductor with straight / drop clamp | set | 63 | 30 | 93 |  | 0
10.3 | 765 kV | Single Suspension | 765kV Single suspension insulator string comprising 1x44 discs with subconductor spacing 450mm suitable for quad Bersimis conductor with straight / drop clamp | set | 6 | 0 | 6 |  | 0
10.4 | 765 kV | Double Tension | 765kV Double tension insulator string comprising 2x44 discs with subconductor spacing 450mm suitable for quad Bersimis conductor with / without turn Buckle | set | 6 | 0 | 6 |  | 0
10.5 | 765 kV |  | Guy wire arrangement (As per enclosed sketch) | set | 5 | 8 | 13 |  | 0
| Bus material & shield wire | [7 empty] | 0
11 | - | AAC Bull Conductor | Conductor complete with Tee connectors for droppers to equipment connections, PG clamps for busbar jumpering, Twin/Quad bundle spacers etc to complete to complete the stringing work are included in the scope | Km | 32 | 14 | 46 |  | 0
12 |  | 4.5" | Al Tube (ETC of Al.Tube includes Aluminium welding and bending to be included. Welding sleeve tube will be supplied by BHEL.) | km | 2 | 1.5 | 3.5 |  | 0
13 | - | 7/9 SWG Sield Wire | GI Stranded Shield wire including tension clamp, PG clamp and clamping on structure for down conductor, fixing/bolting with earth strip etc to complete the earthing connection/stringing work are included in the scope | Km | 4 | 2 | 6 |  | 0
|  |  | . | [5 empty] | 0
0
| Cabling Work | [7 empty] | 0
|  |  | A. Cabling including laying, tagging , dressing, ferruling, lugging, ,soldering, tapping, jointing, crimping, termination, and drilling/ cutting holes in cable gland plates- laying can be either on trays, supports, underground, buried in ground or through GI/PVC pipe over/under ground, through wall etc. All erection materials viz. ferrules, copper lugs, cable ties / straps, Al. tags, markers, GI / PVC wall sleeves with rubber / nylon bushes and flexible steel conduits shall be supplied by bidder. Glands shall be quoted seprately. | [5 empty] | 0
14 |  |  | Control cables | [5 empty] | 0
14.1 |  | PVC | 2Cx2.5 sqmm Cu | Km | 6 | 2 | 8 |  | 0
14.2 |  | PVC | 5Cx2.5 sqmm Cu | Km | 38 | 18 | 56 |  | 0
14.3 |  | PVC | 7Cx2.5 sqmm Cu | Km | 16 | 4 | 20 |  | 0
14.4 |  | PVC | 10Cx2.5 sqmm Cu | Km | 45 | 10 | 55 |  | 0
14.5 |  | PVC | 14Cx2.5 sqmm Cu | Km | 40 | 14 | 54 |  | 0
14.6 |  | PVC | 19Cx2.5 sqmm Cu | Km | 28 | 10 | 38 |  | 0
0
0
15 |  |  | Auxiliary Power cables | [5 empty] | 0
15.1 |  | PVC | 2Cx6 sqmm Al/Cu | Km | 4.5 | 1.5 | 6 |  | 0
15.2 |  | PVC | 4Cx6 sqmm Al/Cu | Km | 10 | 3.5 | 13.5 |  | 0
15.3 |  | PVC | 4Cx16 sqmm Al/Cu | Km | 14 | 4.5 | 18.5 |  | 0
15.4 |  | PVC | 3.5Cx35 sqmm Al/Cu | Km | 0.5 | 0.5 | 1 |  | 0
15.5 |  | PVC | 3.5Cx70 sqmm Al/Cu | Km | 4.5 | 2 | 6.5 |  | 0
0
0
| Cable Glands | [7 empty] | 0
16 |  |  | Supply & installation - Tin/ Nickel, Nichel/chromium - Plated (coating thickness not less than 10 microns) Powergrid approved / Sunil & Co. / Arup/ Comet / QPIE make brass cable glands, double compression heavy-duty type complete with necessary armour clamp & tapered washer etc for the following cables (Bidder's Scope is to supply and fixing) Qty may vary by ±50% | [5 empty] | 0
16.01 |  | PVC/ XLPE | 2Cx2.5 sqmm Cu | Nos. | 200 | 66 | 266 |  | 0
16.02 |  | PVC/ XLPE | 5Cx2.5 sqmm Cu | Nos. | 600 | 200 | 800 |  | 0
16.03 |  | PVC/ XLPE | 7Cx2.5 sqmm Cu | Nos. | 300 | 100 | 400 |  | 0
16.04 |  | PVC/ XLPE | 10Cx2.5 sqmm Cu | Nos. | 300 | 100 | 400 |  | 0
16.05 |  | PVC/ XLPE | 14Cx2.5 sqmm Cu | Nos. | 600 | 200 | 800 |  | 0
16.06 |  | PVC/ XLPE | 19Cx2.5 sqmm Cu | Nos. | 400 | 135 | 535 |  | 0
16.07 |  | PVC/ XLPE | 2Cx6 sqmm Al/Cu | Nos. | 50 | 18 | 68 |  | 0
16.08 |  | PVC/ XLPE | 4Cx6 sqmm Al/Cu | Nos. | 52 | 18 | 70 |  | 0
16.09 |  | PVC/ XLPE | 4Cx16 sqmm Al/Cu | Nos. | 132 | 44 | 176 |  | 0
16.1 |  | PVC/ XLPE | 3.5Cx35 sqmm Al/Cu | Nos. | 6 | 4 | 10 |  | 0
16.11 |  | PVC/ XLPE | 3.5Cx70 sqmm Al/Cu | Nos. | 22 | 8 | 30 |  | 0
0
| Cable Trench Materials | [7 empty] | 0
0
17 |  |  | Cable Rack work includes welding and fabrication of cable racks of mild steel angles( 50x50x6 mm suplied by BHEL) & painted racks (paint suply in scope of bidder) on inserts of trench walls in trenches in switchyard and control room. Cable rack assembly will be of 2/3/4 tier. | MT | 20 | 10 | 30 |  | 0
18 |  |  | Laying of 100/110NB PVC pipe at a depth of 300mm including excavation, backfilling, making and repairing of walls in trenches, cutting, threading, fixing of sockets/ bends where required etc. complete. Both ends of PVC pipe shall be closed . (Payment will be made for the as erected pipe length) | Meter | 5000 | 3000 | 8000 |  | 0
19 |  |  | Laying of 50/65 NB PVC pipe at a depth of 300mm including excavation, backfilling, making and repairing of walls in trenches, cutting, threading, fixing of sockets/ bends where required etc. complete. Both ends of PVC pipe shall be closed . (Payment will be made for the as erected pipe length) | Meter | 7000 | 4200 | 11200 |  | 0
0
20 |  |  | Laying of Cable trays: including bends, tees, elbow, reducers, stiffeners coupler plates, bolting to racks, structure etc. to complete. Scope of minor fabrication is also involved. | [5 empty] | 0
20.1 |  |  | 100 to 150 mm wide, 2.5 M long Perforated type | Meter | 500 | 300 | 800 |  | 0
20.2 |  |  | 100 to 750 mm wide, 2.5 M long Ladder type | Meter | 100 | 60 | 160 |  | 0
0
| STRUCTURE AND EARTHING WORKS | [7 empty] | 0
21 |  |  | Earthing material- The earthing includes earthing of all switchyard equipment, towers, pipe structure, cable trenches, fence, pipe electrode for LA, CVT, neutral of transformer & at interconnections of other grids, Control room equipments using necessary Connectors for earthing flats. Earthing clamping shall be carried out by ETC contractor. GS strip including cutting, bending, welding with 40 mm dia MS rod riser/earth strip, applying zinc rich paint, clamping to structure/building wall etc. to complete. Hardware required for connecting flat on pads of structure & equipment included in scope. The Earthing of equipments, Auxiliary Earthmats under Iso/ ES/ CB MOM boxes shall be carried out as per Powergrid standard earthing drawing. | [5 empty] | 0
21.1 |  |  | 75 x 12 mm GI Flat | kM | 7 | 4.2 | 11.2 |  | 0
21.2 |  |  | 50 x 6 mm GI Flat | kM | 2.5 | 1.5 | 4 |  | 0
21.3 |  |  | 50 x 6 mm MS Flat | kM | 2 | 1.2 | 3.2 |  | 0
21.5 |  |  | 40mm dia MS Rod for equipment risers | MT | 12 | 7.2 | 19.2 |  | 0
0
0
22 | Steel Structure | [7 empty] | 0
22.1 |  |  | Galvanised steel Lattice Structures including hardwares for Towers, beams & equipment support | MT | 1600 | 862 | 2462 |  | 0
22.2 |  |  | Galvanised steel Pipe Structures including hardwares for equipment support | MT | 10 | 1 | 11 |  | 0
0
23 | Control and Relay panels | [7 empty] | 0
|  |  | Testing and commissioning of relays in scope of panel supplier. Necessary manpower support, tools, tackles and testing equipment to be in scope of ETC contractor | [5 empty] | 0
23.1 |  |  | 765 kV Control & Relay Panels : | [5 empty] | 0
23.2 |  |  | 765kV Circuit Breaker Relay Panel with Auto reclose | Set | 5 | 4 | 9 |  | 0
23.3 |  |  | 765kV Circuit Breaker Relay Panel without Auto reclose | Set | 5 | 2 | 7 |  | 0
23.5 |  |  | 765kV Line Protection Panel | Set | 2 | 2 | 4 |  | 0
23.6 |  |  | Transformer Protection Panel (For both HV & MV side) | Set | 2 | 0 | 2 |  | 0
23.7 |  |  | 765kV Reactor Protection Panel | Set | 3 | 2 | 5 |  | 0
23.8 |  |  | 765kV Busbar Protection Panel | Set | 1 | 0 | 1 |  | 0
| FO CABLE LAYING - Contractor's supplied GI Pipe | [7 empty] | 0
24 |  |  | SAS : Armoured Fibre Optic system Cable for SAS and Busbar protection ( to be laid in GI Pipe) ( Scope - Laying of the cables in the 25NB GI PIPE), SUPPLY OF GI PIPE (Powergrid accepted) shall also be in contractor's scope | [5 empty] | 0
24.1 |  |  | Supply and Laying of 25 mm GI pipes( light grade) conduits alongwith socket, bend and joint on trench rack support . Cutting, threading, fixing of clamps sockets/ bends/joints where required etc. complete. Supply of required clamp for fixing GI conduits on Cable rack shall be in ETC contractor scope. (Payment will be made for the as erected pipe length). GI conduits shall be used for laying of fiber optic cables /sensor cables. | M | 5000 | 3000 | 8000 |  | 0
24.2 |  |  | Armoured FO cable along with connectors for SAS & Busbar Protection. The laying of network/optical cables cables shall be in the contractor scope. However, Optical cable will be laid under SAS supplier's supervision. Splicing and Termination shall be in SAS supplier's scope.). FO cable shall be laid in 25mm dia. GI pipes . | M | 8000 | 4800 | 12800 |  | 0
| MKJB CTJB CVTJB | [7 empty] | 0
25 |  |  | Marshalling Kiosks & CT / CVT Junction Boxes | [5 empty] | 0
25.1 |  |  | Bay Marshalling Kiosks ( Outdoor, Floor mounted on cable trench) | Nos. | 8 | 4 | 12 |  | 0
25.2 |  |  | CT Junction Box (on CT structure) | Nos. | 8 | 4 | 12 |  | 0
25.3 |  |  | CVT Junction Box (on CVT structure/ on foundation) | Nos. | 4 | 2 | 6 |  | 0
0
26 |  |  | Installation of terminal connectors at customer supplied/erected items whereas erection of equipments are not in scope of contractor. Terminal connectors shall be provided by BHEL. Any other ETC works related to items below is not in the scope of this BOQ. | [5 empty] | 0
26.1 |  |  | 765 KV single phase reactors | No | 7 | 6 | 13 |  | 0
26.2 |  |  | 765 KV single phase Transformer | No | 7 | 0 | 7 |  | 0
0
27 |  | SUPPLY INCLUDED | SUPPLY AND INSTALLATION OF ISMC 100, ISMC 50 for Panel Supports | MT | 1 | 1 | 2 |  | 0
|  |  | Total Amount (Rs.) | [5 empty] | 0
Following also forms the scope of ETC work in addition to above, but not limited to this.
1 | Assembly, installation, pre-commissioning test and commissioning tests (As per BHEL FQP) are included in the scope.
2 | Annexure- 2 (Switchyard Erection guidelines) shall be followed for ETC work.
3 | All the drawings and documents as per Annexure-1 shall be followed for ETC work.
4 | Minor Civil works such as modification of civil foundations, making holes in the trenches/ control room building, grouting, fixing of trench material will be in the scope of ETC contractor.
5 | Removal of gravel, if gravelling is done, for connection of Equipment earthing strip to the existing mat (wherever earthing mat is already laid), and after completion of earthing , contractor should place the gravel to bring it in original shape.
6 | The quantities given in items mentioned above may undergo a change to any extent.
7 | Quoted rates are deemed to be inclusive of miscellaneous works viz erection of clamps and connectors.
8 | All paint , welding electrodes & other consumable by contract supplies shall be part of ETC works. Paint /welding electrode make etc. is subject to BHEL/CUSTOMER site incharge approval.
9 | Equipment erection (say Isolator ) means complete erection, metallics, post insulator, connectors (expansion/rigid tubular for Al.Tube / single/double/quadraple conductor), connection to the next in line (if connected to overhead busbar or droppers) including PG clamps/Tee connectors etc. This will be clear from the enclosed electrical layout drawings.
10 | Equipment and tower erection would include supply and erection of miscellanneous items , viz Phase colour discs , labels painting of equipments , phase colour painting , phase marking , bay identification board , danger plates , rubber mats , device number marking on the equipment, keyboard etc as per site requirements. Supply & Mounting of phase color discs & Danger plates shall be as per IS-2551; 1982 & IS 5; 1978.
11 | Welding of Aluminium tubes ( supply of welding sleeve excluded) as per Annexure-3 is in ETC contractor's scope and joints shall be tested by radiography. Welding and Bending machines and any other equipment will be in ETC Contractor scope.
12 | Completete ETC package is under the scope of bidder. All TNP including oil filterating machine, cranes etc. required to complete the job shall be provided by bidder only.
13 | Testing istruments (dully calibrated) have to be arranged by ETC Contractor at it's own cost ( List is only provided for information , if any other instrument not mentioned below but required for sucessful completion of ETC work shall be in ETC contractor's scope) , (However OMICRON or equivalent kit for Numerical relay testing shall be arranged by BHEL.)
13.1 | DCRM (OPERATIONAL ANALYZER )
13.2 | Contact Resistance Measurement kit (CRM)
13.3 | Capacitance and Tan delta measurement Kit
13.4 | Dew Point Measurement kit
13.5 | 5kV/1kV Megger
13.6 | Primary current Injection Kit
13.7 | Secondary current/Voltgae Injection kit
13.8 | 1Ph Variac
13.9 | Multimeters
13.1 | Clamp on meter
13.11 | Relay test kit
14 | The scope of supply items as mentioned in above BOQ are tentative . Items shall be supply by contractor as per exact site requiremnets only.
15 | For scope of supply items in ETC contractor scope following should be followed . (1)The approval of makes shall be obtained from BHEL/Customer . (2)Drawings and MQP shall be submitted for approval in line with specification and relevant IS. (3) Quality -Inspection & dispatch clearance shall be given by BHEL/Customer.