ANNEXURE I

SCOPE OF WORK.

PREVENTIVE AND BREAKDOWN   MAINTENANCE OF RECIPROCATING  COMPRESSORS (34 NOS) AND SCREW COMPRESSORS(10 NOS) IN TCB, &  NEW  TRANFORMER BLOCK III.

NO. OF PREVENTIVE MAINT=88, TO BE DONE  IN A YEAR ACCORDING TO SHEDULE.

- Checking for oil leaks. Checking of compressor oil for optimum operating level, topping up upto specified levels, inspecting  through sight  window Rectify accordingly

- Before starting the machine  checking the inlet position of  butterfly for 020.00 degrees  in inlet wide position,OFF- VRERTICAL.

3) Checking the electrical connections of motor and automatic pressure for being through starter.

4) Checking lubricant level every day maintain it at correct level.

5) Drain receiver tank condensate (if automatic draining device is not provided). Open manual drain valve and collect  and dispose of condensate accordingly.

6)Adjusting the load sump pressure  control stop screw until sump pressure gauge reads 04.00 Kg/cm2

7) Check for unusual noise and vibration.

8) Checking electrical connection for tightness

9) Checking compressor foundation bolts for looseness.

10) Ensure belt guards and covers are securely in place.

11) Checking of all the hose pipe etc for leakages

12)Checking of motor to compressor coupling.

13)Checking of all the gauges.

14)Checking of air filters for any restriction. Clean air filter element folds carefully by directing a jet of dry compressed air  at not more than  4 Kg/sq cm to outside the element

15)Remove and clean the compressor bearing oil filter housing  which is mounted in the pipe from the oil separator  to the pump inlet

16) Changing bearing oil  filter element  if pressure drop is more than  01.00 Kg/cm2

17) Ensure area around compressor is free from rags, tools, debris, and flammable or explosive materials.

18) Check all the valves. These should be properly cleaned.

19) Refitting the valves  & ensure these are properly fitted.

20) Checking the thermal valve

21) Cleaning coolant filter DELTA –P when clogged

22) Observe operation of safety valves while the compressor is running. Replace safety valves that do not operate freely.

23) Checking the pressure switch for being adjusted to the designed pressure, adjust if necessary.

24)Check  shut down pressure

25) Checking and rectifying belt wheel looseness or excessive end play in motor shaft.

26) Inspect for air leaks. Squirt soapy water around joints during compressor operation and watch for bubbles.

27) Check tightness of screws and bolts. Tighten as required.

28) Tightening the separator cover bolts @ 200 Nm

29) Inspect drive belts. Adjust if necessary. Clean exterior.

30) Drain out all the lubricant from the crank case. Change lubricant with correct grade while crankcase is warm.

31) Clean sight glass Replace oil filter and (if necessary) on pressure lubricated models

32)Blow off the dirt from the radiator oil cooler sections with a jet of air directed on them from the out side. (The plant must not be running during this operation).

33)Checking the functioning of safety valve. Setting if required

34) Dismantle and clean concentric valve plate and spring plate,change if necessary

35) Checking alignment of V - belts.Checking the tension of V belts. Adjusting sheave within 016.00 mm deflection.

36) Dismantle the oil cooler section fitted in front of the  radiator and clean internally and externally.

DYMGR(FRX)