## PRICE FORMAT-UN-PRICED
PRICE FORMAT (UN-PRICED)
ITEM: LT Switchgear Item and site modification work for 2x250MW Bhavnagar
TENDER REF: 12300903
All values in INR
NAME OF BIDDER: M/S. ______________
Sl.No | Material code | Item Description | HSN CODE (To be mentioned by Bidder) | U/M | Qty. | Unit Ex-Works Price Incl. Packing Charges | Total Ex-Works Price Incl. Packing Charges | Total Freight Price | Total Price Incl. Freight | CGST @ | SGST @ | IGST @ | Total FOR Price
[10 empty] | 0% | 0% | 0%
[5 empty] | (1) | (2) | (3)=(1)x(2) | (4) | (5)=(3)+(4) | (6)=(5)x CGST% | (7)=(5)x SGST% | (8)=(5)x IGST% | (9)=(5)+(6)+(7)+(8)
1 | ELBHAVSUP01 | Supply of BOQ as per Annexure-A |  | LOT | 1 |  | 0 |  | 0 | 0 | 0 | 0 | 0
2 | ELBHAVSER01 | Site Modification as per Annexure-B |  | LOT | 1 |  | 0 |  | 0 | 0 | 0 | 0 | 0
A | TOTAL FOR PRICE FOR ALL LINE ITEMS OF A (Sr. No. 1 to 2) | [11 empty] | 0
B | LESS TOTAL GST CREDIT | [11 empty] | 0
C | LANDED COST FOR EVALUATION PURPOSE ONLY | [11 empty] | 0

## Annexure-A
2X 250 MW BHAVNAGAR
BOQ CUM PRICE SCHEDULE FOR LT SWITCHGEAR
ANNEXURE-A
S. No. | DESCRIPTION | UNIT | QTY. | UNIT PRICE | TOTAL PRICE | BRIEF SPECIFICATION
1 | FUSE LINKS FOR DC FEEDERS |  |  |  |  | SUITABLE FOR HRC DIN TYPE FUSE OF L&T MAKE. SCHEME-X. TO BE FITTED IN VARIOUS MODULES OF SWITCHBOARD 1FA, 2FA & 0FA.
i. | 2A | Nos. | 25
ii. | 6A | Nos. | 100
iii. | 10A | Nos. | 15
iv. | 16A | Nos. | 15
v. | 25A | Nos. | 30
vi. | 32A | Nos. | 40
vii. | 40A | Nos. | 10
viii. | 50A | Nos. | 10
ix. | 63A | Nos. | 10
x. | 100A | Nos. | 15
xi. | 200A | Nos. | 8
xii. | 315A | Nos. | 8
xiii. | 400A | Nos. | 5
2 | PUSH BUTTON
i. | EMERGENCY STOP PUSH BUTTON | Nos. | 130 |  |  | PB STAY PUT MUSHROOM HEAD PRESS TO LOCK & KEY TO RELEASE OF L&T MAKE OR EQUIVALENT. PB SHALL BE SUITABLE FOR TYPE – A (EMG. STOP LPBS) OF UNILEC MAKE.
ii. | EMERGENCY STOP PUSH BUTTON & START PUSH BUTTON | Nos. | 5 |  |  | PB STAY PUT MUSHROOM HEAD PRESS TO LOCK & KEY TO RELEASE OF L&T MAKE OR EQUIVALENT. PB SHALL BE SUITABLE FOR TYPE – B (START & EMG. STOP LPBS) OF UNILEC MAKE.
iii. | EMERGENCY STOP PUSH BUTTON | Nos. | 2 |  |  | PB STAY PUT MUSHROOM HEAD PRESS TO LOCK & KEY TO RELEASE OF L&T MAKE OR EQUIVALENT. PB SHALL BE SUITABLE FOR TYPE – C (FLAME PROOF STOP) OF UNILEC MAKE.
3 | PT FUSE FAILURE RELAY | Nos. | 4 |  |  | PTR-110V AC, AUX. SUPPLY 220V DC WITH 1NO+1NC CONTACTS, UVT92, ABB MAKE
4 | TIME DELAY RELAY | Nos. | 2 |  |  | TIME DELAY RELAY, DELAY ON PICK UP, 0.1-1 SEC, AUX SUPPLY 220V DC WITH 3NO + 1 NC CONTACTS. ABB MAKE.
5 | DC OVERVOLTAGE RELAY | Nos. | 1 |  |  | DC OVERVOLTAGE RELAY VAG11, MAKE: AREVA
6 | POWER CONTACTOR | Nos. | 2 |  |  | IN TURBINE MCC 1KA & 2KA, CONTACTORS (OF 18A) ARE REQUIRED IN THE 3 PHASE HEATER MODULE, MAKE L&T.
7 | SFU HANDLE | Nos. | 2 |  |  | HANDLE OF DOOR IS NOT PRESENT IN 1HA-17B, 1HA-17C OF 32A SFU.
8 | HT METALLIC DOOR LOCK | Nos. | 150 |  |  | SUITABLE FOR FITTING IN LT SWITCHGEAR OF UNILEC MAKE.
9 | DOOR LOCKS OF PLASTIC C-TYPE | Nos. | 100 |  |  | SUITABLE FOR FITTING IN LT SWITCHGEAR OF UNILEC MAKE.
10 | DOOR LOCKS OF PLASTIC Z-TYPE | Nos. | 100 |  |  | SUITABLE FOR FITTING IN LT SWITCHGEAR OF UNILEC MAKE.
11 | POWER CONTACTOR | Nos. | 3 |  |  | POWER CONTACTOR OF 265A OF L&T MAKE TO BE FITTED IN 1HA-17D, 1HA-17T & 1HA-17R
12 | POWER CONTACTOR | Nos. | 3 |  |  | POWER CONTACTOR OF 70A OF L&T MAKE TO BE FITTED IN 1EA-09C, 1EA-09D & 1EA-10S.
13 | AUXILIARY CONTACTOR | Nos. | 3 |  |  | AUXILIARY CONTACTOR (2NO +2 NC) SUITABLE FOR 110V AC OF L&T MAKE TO BE FITTED IN 1EA-09C, 1EA-09D & 1EA-10S.
14 | AL GLAND PLATE | Nos. |  |  |  | FOR VARIOUS 1CORE CABLES,GLAND PLATE SHALL BE OF NON-MAGNETIC MATERIAL. REMOVABLE GLANDS PLATES OF THICKNESS 4.0 mm (NON-MAGNETIC MATERIAL) SHALL BE PROVIDED.
| 700mm X 290mm | Nos. | 15
| 340mm X 210mm | Nos. | 20
| 500mm X 290 mm | Nos. | 25
15 | DUMMY PLATE | Nos. | 1 |  |  | IN 2EA, 1 DUMMY PLATE TO BE FITTED. DIMENSIONS ARE: 150 x 550.
16 | SEAL POT BLOWER (Module Type - DK21) | Nos. | 1 |  |  | SEAL POT BLOWER (90KW) SPARE FEEDER IN 1HA-17R. M/s UNILEC MAKE TROLLEY WITH 250A SFU MODULE TO BE SUPPLIED. DK21 SCHEME FOR REFERENCE IS ATTACHED ACCESSORIES SUCH AS CHANNEL RAIL, MAIL & FEMAIL CONTACT FOR I/C AND O/G, SUPPORT, GASKET, SHROUD FOR SHUTTER, TROLLEY CONNECTOR BUSBAR FOR I/C & O/G, FRONT DOOR ETC. SHALL BE PART OF TROLLEY + MODULE. TROLLEY FRAME CRCA SHEET STEEL THICKNESS SHALL BE 2.0MM AND FOR DOOR IT SHALL BE 1.6MM. IN THIS REGARD REFER DETAIL AT ANNEXEXURE-B ALSO.
17 | 7.5kW DOL Starter Feeder, Scheme no. DK2 / 416 | Nos. | 4 |  |  | M/s UNILEC MAKE TROLLEY TO BE SUPPLIED. SCHEME FOR REFERENCE IS ATTACHED ACCESSORIES SUCH AS CHANNEL RAIL, MALE & FEMALE CONTACT FOR I/C AND O/G, SUPPORT, GASKET, SHROUD FOR SHUTTER, TROLLEY CONNECTOR BUSBAR FOR I/C & O/G, FRONT DOOR ETC. SHALL BE PART OF TROLLEY + MODULE. TROLLEY FRAME CRCA SHEET STEEL THICKNESS SHALL BE 2.0MM AND FOR DOOR IT SHALL BE 1.6MM. IN THIS REGARD REFER DETAIL AT ANNEXEXURE-B ALSO.
18 | 3.7kW DOL Starter Feeder, Scheme no. K 3 / 425 | Nos. | 4
19 | 100A SFU O/G Feeder, Scheme no. E / 438 | Nos. | 1
20 | upto 5.5kW Dual Speed Bidirectional Motor Feeder (Module Type - DS) | Nos. | 4
21 | Module Type - DW for 220V DC DB (0.05KW) | Nos. | 2
22 | Module Type - E (63A) | Nos. | 16
23 | Module Type- DK2 (11 KW) | Nos. | 2
24 | Module Type - E (16A) | Nos. | 8
25 | Module Type - E (32A) | Nos. | 10
26 | Module Type - X (6A) | Nos. | 8
27 | Module Type - X (16A) | Nos. | 8
28 | Module Type - X (100A) | Nos. | 2 |  |  | RATING OF DC SEAL OIL PUMP TO BE CONSIDERED AS 100A. FOR MAIN FEEDER SPARE OF DC EOP HAS BEEN CONSIDERED BY PSWR. THIS ADDITIONAL MODULE MAY PLEASE BE CONSIDERED AS SPARE OF DC SEAL OIL PUMP. IN THIS REGARD REFER DETAIL AT ANNEXEXURE-B ALSO.
29 | Module Type - X (160A) | Nos. | 4 |  |  | RATING OF DC EMERGENCY OIL PUMP TO BE CONSIDERED AS 150A OR GREATER. THIS ADDITIONAL MODULE MAY PLEASE BE CONSIDERED AS SUPPLY FEEDER & SPARE OF DC EMERGENCY OIL PUMP. IN THIS REGARD REFER DETAIL AT ANNEXEXURE-B ALSO.
30 | HRC Fuse
| 16A | Nos. | 9 |  |  | M/s L&T MAKE
| 63A | Nos. | 12 |  |  | M/s L&T MAKE
31 | Over Load Relay |  |  |  |  | M/s L&T MAKE
| 0.3 - 0.5A (0.06KW) | Nos. | 2 |  |  | M/s L&T MAKE
| 2 - 2.3 A | Nos. | 4 |  |  | M/s L&T MAKE
| 3 - 5A (1.5KW) | Nos. | 3 |  |  | M/s L&T MAKE
| 14-23A | Nos. | 4 |  |  | M/s L&T MAKE
32 | Switch Fuse Unit
| 63A | Nos. | 4 |  |  | M/s L&T MAKE
33 | Power Contactor
| 32A | Nos. | 4 |  |  | M/s L&T MAKE
34 | Air Circuit Breaker
| 630 A | Nos. | 2 |  |  | M/s L&T MAKE. TG-DMCW C MOTOR FEEDERS BREAKER REPLACEMENT AND BOILER FILL PUMP DRIVE MOTOR FEEDER BREAKER REPLACEMENT.
35 | Bus PT of R Phase | Nos. | 1 |  |  | M/s INDCOIL MAKE, PRIMARY: 415/√3, SECONDARY:110 /√3, 100 VA, INSULATION: E, CLASS: 1. TO BE FITTED IN BUS PT OF BOILER MCC 2HA SECTION-B.
36 | Trip Coil of Air Circuit Breakers (1600A, 100VA) | Nos. | 10 |  |  | M/s L&T Make of Unit-2 of Bhavnagar TPP.
37 | Series Resistance (4K ohm, >=30W) of the Trip Coil of Air Circuit Breakers (1600A, 100VA) | Nos. | 10 |  |  | M/s L&T Make of Unit-2 of Bhavnagar TPP.
38 | JAW Contacts of Air Circuit Breaker of 1600A | Set | 1 |  |  | Suitable for ACB (of 1600A) of M/s L&T Make.

## Annexure-B
( 2 x 250MW BHAVNAGAR TPS)
SITE MODIFICATION
ANNEXURE-B
SL NO | DESCRIPTION OF FEEDER | BOARD NAME, MODULE | KW/A GIVEN IN MCC / CABLE SIZE | REVISED KW/A RATING / CABLE SIZE | OLD MODULE POSITION | MOTOR AMPS(FLC) | ADDITION IN COMPONENT (TO BE FILLED BY KMG ATOZ) | USE COMPONENT FROM (SLN.) / Req. | DELETION IN COMPONENT (TO BE FILLED BY KMG ATOZ) | USE COMPONENT TO (SLN.) | NEW MODULE POSITION | REMARK | PURPOSE
1 | Oil supply unit / Hydraulic Power Unit of HP Bypass System | 1KA, 2KA | - | 7.5 KW / 3C X 25 sq.mm | - | [6 empty] | 1 New Modules to be inserted in both the boards. Scheme Type DK2.
2 | Spare | 1KA, 2KA | - | 7.5 KW / 3C X 25 sq.mm | - | [6 empty] | 1 New Modules to be inserted in both the boards. Scheme Type DK2.
2 | OW Sump Pump | 0SA | 1.1 / 3C X 2.5 sq.mm | 1.5 / 3C X 2.5 sq.mm | 01B, 09B | [5 empty] | 01B, 09B | Scheme type same as per approved drawing.Rating Change
3 | OW Separator Sump Pump | 0SA | 1.1 / 3C X 2.5 sq.mm | 1.5 / 3C X 2.5 sq.mm | 09R | [5 empty] | 09R | Scheme type same as per approved drawing.Rating Change
4 | Electrical Heat Tracing Panel | 0SA | 63 A / 3.5C X 25 sq.mm | 100 A / 3.5C X120 sq.mm | 02B | [5 empty] | 09C | Scheme type same as per approved drawing.Rating Change
5 | Clean Lube Oil Transfer Pump | 0DA | - | 3.7 KW / 3C X 10 sq.mm. | - | [6 empty] | 1 New Modules to be inserted in both the boards. Scheme Type K3.
6 | Dirty Lube Oil Pump | 0DA | - | 3.7 KW / 3C X 10 sq.mm. | - | [6 empty] | 1 New Modules to be inserted in both the boards. Scheme Type K3.
7 | Drain Oil Lube Transfer Pump | 0DA | - | 3.7 KW / 3C X 10 sq.mm. | - | [6 empty] | 1 New Modules to be inserted in both the boards. Scheme Type K3.
8 | Spare | 0DA | - | 3.7 KW / 3C X 10 sq.mm. | - | - | - | - | - | - |  | 1 New Modules to be inserted in both the boards. Scheme Type K3.
9 | Emergency Cooling Water to Spiess Valve (BACW-95) | 1KB, 2KB | 0.18 KW / 3C X 2.5 | 0.06 KW / 3C X 2.5 | 33R | [5 empty] | 33R | Scheme type same as per approved drawing.Rating Change
10 | CW Supply Isolation Valve (BACW-01) | 1KB, 2KB | 1.2 KW / 3C X 2.5 | 0.52 KW / 3C X 2.5 | 30S | [5 empty] | 30S | Scheme type same as per approved drawing.Rating Change
11 | CW Return Isolation from Spiess Valve to Pit (BACW-03) | 1KB, 2KB | 1.2 KW / 3C X 2.5 | 0.52 KW / 3C X 2.5 | 32P | [5 empty] | 32P | Scheme type same as per approved drawing.Rating Change
12 | CW Return Isolation from Spiess Valve to Pit (BACW-96) | 1KB, 2KB | 0.18 KW / 3C X 2.5 | 0.09 KW / 3C X 2.5 | 33P | [5 empty] | 33P | Scheme type same as per approved drawing.Rating Change
13 | Sequence Trimming Device | 1FA, 2FA | 0.05 KW | 0.05 KW | 04W | [5 empty] | 04W | Scheme to be revised.
14 | Lignite Air Lock Feeder | 1HA,2HA | - | - | - | [5 empty] | - | Change of Scheme to Dual Speed Drive
15 | SPACE HEATING TO 6.6kV SWITCHGEAR #1CA MODULE 1CA | 0DA | - | 32A / 3.5C x 25 sq.mm. | - | [5 empty] | - | 1 New Modules to be inserted in the board. Scheme Type E.
16 | SPACE HEATING TO 6.6kV SWITCHGEAR #1CB MODULE 1CB | 0DA | - | 32A / 3.5C x 25 sq.mm. | - | [5 empty] | - | 1 New Modules to be inserted in the board. Scheme Type E.
17 | SPACE HEATING TO 6.6kV SWITCHGEAR #2CA MODULE 2CA | 0DA | - | 32A / 3.5C x 25 sq.mm. | - | [5 empty] | - | 1 New Modules to be inserted in the board. Scheme Type E.
18 | SPACE HEATING TO 6.6kV SWITCHGEAR #2CB MODULE 2CB | 0DA | - | 32A / 3.5C x 25 sq.mm. | - | [5 empty] | - | 1 New Modules to be inserted in the board. Scheme Type E.
19 | SPACE HEATING TO 6.6kV SWITCHGEAR #0CA MODULE 0CA | 0DA | - | 32A / 3.5C x 25 sq.mm. | - | [5 empty] | - | 1 New Modules to be inserted in the board. Scheme Type E.
20 | SPACE HEATING TO 6.6kV SWITCHGEAR #0CB MODULE 0CB | 0DA | - | 32A / 3.5C x 25 sq.mm. | - | [5 empty] | - | 1 New Modules to be inserted in the board. Scheme Type E.
21 | SPACE HEATING TO 6.6kV SWITCHGEAR #0CC MODULE 0CC | 0DA | - | 32A / 3.5C x 25 sq.mm. | - | [5 empty] | - | 1 New Modules to be inserted in the board. Scheme Type E.
22 | SPACE HEATING TO 6.6kV SWITCHGEAR #0CD MODULE 0CD | 0DA | - | 32A / 3.5C x 25 sq.mm. | - | [5 empty] | - | 1 New Modules to be inserted in the board. Scheme Type E.
23 | CONTROL FLUID PUMP-1 IN HPSU | 1KA04S | 7.5 KW / 3C X 10 sq.mm. | 11 KW / 3.5C X 25 sq.mm. | 1KA04S | [5 empty] | 1KA04S | Scheme type same as per approved drawing.Rating Change
24 | CONTROL FLUID PUMP-2 IN HPSU | 1KA11S | 7.5 KW / 3C X 10 sq.mm. | 11 KW / 3.5C X 25 sq.mm. | 1KA11S | [5 empty] | 1KA11S | Scheme type same as per approved drawing.Rating Change
25 | CONTROL FLUID PUMP-1 IN HPSU | 2KA04S | 7.5 KW / 3C X 10 sq.mm. | 11 KW / 3.5C X 25 sq.mm. | 2KA04S | [5 empty] | 2KA04S | Scheme type same as per approved drawing.Rating Change
26 | CONTROL FLUID PUMP-2 IN HPSU | 2KA11S | 7.5 KW / 3C X 10 sq.mm. | 11 KW / 3.5C X 25 sq.mm. | 2KA11S | [5 empty] | 2KA11S | Scheme type same as per approved drawing.Rating Change
27 | Spare | 1KA | - | 11 KW / 3.5C X 25 sq.mm. | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type DK2.
28 | Spare | 2KA | - | 11 KW / 3.5C X 25 sq.mm. | [7 empty] | 1 New Modules to be inserted in the boards. Scheme Type DK2.
29 | CONTROL FLUID CIRCULATING PUM P-1 IN HPSU | 1KA01F | 0.37 KW / 3C X 2.5 sq.mm. | 1.1 KW / 3.5C X 2.5 sq.mm. | 1KA01F | 1KA01F | 1KA01F | 1KA01F | 1KA01F | 1KA01F | 1KA01F | Temporarily resolution as provided to site is: "PEM Reply: Consider modules 1KA/01C/23 and 2KA/01C/23 to be inserted in module position 1KA/01F/20 and 1KA/13E/68. Same cable size as 3C x 2.5 sq.mm. to be used."
30 | CONTROL FLUID CIRCULATING PUM P-2 IN HPSU | 1KA13E | 0.37 KW / 3C X 2.5 sq.mm. | 1.1 KW / 3.5C X 2.5 sq.mm. | 1KA13E | 1KA13E | 1KA13E | 1KA13E | 1KA13E | 1KA13E | 1KA13E
31 | CONTROL FLUID CIRCULATING PUM P-1 IN HPSU | 2KA01F | 0.37 KW / 3C X 2.5 sq.mm. | 1.1 KW / 3.5C X 2.5 sq.mm. | 2KA01F | 1KA01F | 1KA01F | 1KA01F | 1KA01F | 1KA01F | 2KA01F | Scheme type same as per approved drawing.Rating Change
32 | CONTROL FLUID CIRCULATING PUM P-2 IN HPSU | 2KA13E | 0.37 KW / 3C X 2.5 sq.mm. | 1.1 KW / 3.5C X 2.5 sq.mm. | 2KA13E | 1KA13E | 1KA13E | 1KA13E | 1KA13E | 1KA13E | 2KA13E | Scheme type same as per approved drawing.Rating Change
33 | Spare | 1HA | - | 32 A / 3.5C X 25 sq.mm. | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type E.
34 | Spare | 2HA | - | 32 A / 3.5C X 25 sq.mm. | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type E.
35 | Spare | 1FA | - | 6 A /2R X 1C X 10 sq.mm | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type X.
36 | Spare | 1FA | - | 6 A /2R X 1C X 10 sq.mm | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type X.
37 | Spare | 1FA | - | 16 A /2R X 1C X 35 sq.mm | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type X.
38 | Spare | 1FA | - | 16 A /2R X 1C X 35 sq.mm | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type X.
39 | Spare | 2FA | - | 6 A /2R X 1C X 10 sq.mm | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type X.
40 | Spare | 2FA | - | 6 A /2R X 1C X 10 sq.mm | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type X.
41 | Spare | 2FA | - | 16 A /2R X 1C X 35 sq.mm | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type X.
42 | Spare | 2FA | - | 16 A /2R X 1C X 35 sq.mm | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type X.
43 | Spare | 0FA | - | 6 A /2R X 1C X 10 sq.mm | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type X.
44 | Spare | 0FA | - | 6 A /2R X 1C X 10 sq.mm | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type X.
45 | Spare | 0FA | - | 6 A /2R X 1C X 10 sq.mm | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type X.
46 | Spare | 0FA | - | 6 A /2R X 1C X 10 sq.mm | - | [5 empty] | - | 1 New Modules to be inserted in the boards. Scheme Type X.
47 | Spare | 1EA | - | 16A | - | [5 empty] | - | 1 New Modules to be inserted in the board. Scheme Type E. | CJJ11
48 | Spare | 2EA | - | 16A | [7 empty] | 1 New Modules to be inserted in the board. Scheme Type E. | CJJ11
49 | UNDER SLUNG CRA NE FOR ID FANS | 1HA16S | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
50 | LIFTING HOIST FOR PA FAN2 MOTOR | 1HA16P | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
51 | LIFTING HOIST FOR PA FAN1 MOTOR | 1HA04U | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
52 | LIFTING HOIST FOR SA FAN2 MOT OR | 1HA15T | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
53 | LIFTING HOIST FOR SA FAN1 MOT OR | 1HA04T | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
54 | UNDER SLUNG CRA NE FOR BLOWER R OOM | 1HA16Q | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
55 | LEVELING HOIST FOR RAPH | 1HA06S | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
56 | LEVELING HOIST FOR RAPH | 1HA17R | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
57 | UNDER SLUNG CRA NE FOR ID FANS | 2HA16S | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
58 | LIFTING HOIST FOR PA FAN2 MOTOR | 2HA16P | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
59 | LIFTING HOIST FOR PA FAN1 MOTOR | 2HA04U | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
60 | LIFTING HOIST FOR SA FAN2 MOT OR | 2HA15T | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
61 | LIFTING HOIST FOR SA FAN1 MOT OR | 2HA04T | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
62 | UNDER SLUNG CRA NE FOR BLOWER R OOM | 2HA16Q | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
63 | LEVELING HOIST FOR RAPH | 2HA06S | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
64 | LEVELING HOIST FOR RAPH | 2HA17R | 32A | 63A / 3.5C x50 sq.mm | [7 empty] | Rating of Supply feeders to be changed in specified module.
65 | SEAL POT BLOWER | 1HA17T | - | 90KW / 3.5C X 240 sq.mm | [7 empty] | 1 New Modules to be inserted in the board. Scheme Type DK21.

## Annexure-C
ANNEXURE-C
ADDITION / DELETION UNIT PRICES
SL.NO. | ITEM DESCRIPTION | UNIT PRICE
1
2
3
4
5
NOTES:
1) UNIT PRICES OF ALL ELECTRICAL EQUIPMENT REQUIRED IN THE TENDER SHALL BE QUOTED.
2) THESE PRICSE SHALL BE VALID FOR A PERIOD OF ONE YEAR FROM THE DATE OF PURCHASE ORDER.