| Sl. No. | Equipment Description | BHEL Scope | BIDDER Scope |
| --- | --- | --- | --- |
| 1. | Power Cum Control Panel (PDB) for Coal Lab Equipment’s. | BHEL will arrange the required 415 V, 3 phase, 3-wire power supply up to PDB. Power and control/ instrumentation cabling up to PDB shall be by BHEL. Erection of PDB is in the scope of BHEL and balance items erection will be in the scope of bidder. Power Cable (2/3Cx 2.5 CU, 3CX6/10/16/25/35 AL) between PDB and Coal lab equipment’s will be supplied by BHEL. Cabling between PDB and individual equipment will be in the scope of BHEL. Earth pit/grid/mat of Coal lab equipment is in the scope of BHEL. Air Conditioning of Coal Lab is in the scope of BHEL. Bidder has to submit the heat load details of the supplied equipment’s. | Further distribution of required Power supply (including providing control transformer for 230V AC, 110V AC/DC,24V AC/DC etc.) is in the scope of bidder. UPS power requirement (if any) for the system will be in the scope of bidder. Required rating of UPS along with batteries shall be supplied by bidder. Incoming power supply for UPS shall be considered from PDB. Local Power Socket required (if any) will be in the scope of bidder. Total Power requirement for system shall be informed by bidder. PC, Printer required for equipment’s shall be in the scope of bidder. Local Push button stations (if required) shall be provided for all equipment’s supplied by bidder. Any special cable required shall be in the scope of bidder. Bidder has to submit the Power/Control Cable schedule for system. Electrical and Electronic earthing requirement shall be informed by bidder. All Electrical items (including Spares) shall be supplied as per Annexure-01A. |
|  |  |  | Inspection and Testing: All the offered electrical equipment’s shall be Tested and Inspected at manufacturer works as per approved QAP. However, QAP shall be subjected to approval of RRVUNL/TCE. Cost towards the inspection of indigenous / Offshore equipment’s by RRVUNL / TCE Engineer/Inspector will be to Bidder’s account, which includes to & fro Airfare /Railway/ Road fare charges, Boarding and Lodging, local transportation and other related expenses. The cost shall be included in the price. |

ADDITIONAL NOTES

- Makes of all electrical equipment shall be as per approved vendor list furnished by BHEL. If for any equipment, makes are not specified, prior BHEL/RRVUNL approval to be obtained for that sub-vendor.

- Bidder should obtain prior customer approval for make, GA, OGA, schematics, data sheet, QAP for all sub vendor items.

- Base frames, foundation bolts, both half couplings for all equipment shall be in the scope of bidder.

- Training of Customer and BHEL personnel for operation and maintenance of bidder supplied equipment’s is included in the bidder’s scope.

- All the instruments/equipment’s including transmitters, transducers, temperature elements, switches which are required for system is in the scope of bidder.

- bidder’s cable schedule shall be prepared in BHEL format which will be furnished during detailed engineering stage.

- Any festoon/trailing/flexible cables required for this package shall be by bidder.

- Wherever power JB (PJB) is required for termination of cables for motors/drives/equipment, the same shall be in scope of the bidder.

- Type test reports shall be submitted as per specification wherever applicable. In case of non-availability of type test reports for the similar rating/type, shall be conducted without any commercial implication. The Type test certificate shall have minimum 5 years validity from the date of PO.

- Erection (excluding PDB), Testing and Commissioning of bidder supplied equipment/systems is in bidder’s scope.

- Bidder to submit Manuals and Catalogues supplied equipment/systems.

- In case of any conflict & ambiguity, decision of BHEL/customer shall be final and binding.

Vendor List:

| Name of Item | Name of Vendor |
| --- | --- |
| Power Cum Control Panel (PDB) | L&T, Mumbai/ Siemens Ltd, Mumbai/ UNILEC/ GE/ C&S Electric Ltd, New Delhi/ ABB Ltd / Schneider Electric/ Control Switchgear Co New Delhi/ Areva/ RYB Switchgears Ltd. |
| Relays For Switchgears | Alstom T&D India Ltd/ Schneider Electric Infrastructure, France/ ABB Ltd/ Areva T&D |
| Selector Switches & Control Switches | KAYCEE/ Siemens/ Alstom/ L&T/Salzer |
| Push Button | L&T Control And Automation/ Bharatiya Cutler Hammer, Mumbai/ Siemens Ltd/ Tele Mechanic/ Honeywell |
| MCCB/MPCB | C&S/ L&T |
| Control Transformer | Kappa/IndCoil/Precise/Southern Electrical |
| Current Transformer | Pragati/Prayog/Precise/G&M |
| Potential Transformer | Pragati/Prayog/Precise/G&M |
| Indicating lamps | L&T/ Siemens/Teknic/Binay/Rass controls |
| MCB | Siemens/ Havells/ Hager/ ABB Ltd/ L&T |
| Electrical Panel Meter (Ammeter, Voltmeter) | Automatic Electric/ MECO/ Rishabh Instruments |
| Cable Lugs & Glands | Dowels/ Comet |
| Terminal Blocks | Phoenix/ Weidmueller/ Wago/ Elmex/Connect well |
| Switch Socket | Schneider/Anchor/BCH/Best & Crompton |