| COPYRIGHT AND CONFIDENTIAL The information on this document is the property of BHARAT HEAVY ELECTRICALS LIMITED, It must not be used directly or indirectly in any way detrimental to the interest of the company. | JOB SPECIFICATION FOR TILTED PLATE INTERCEPTOR |
| --- | --- |

- GENERAL

The specification covers details of Tilted Plate Interceptor (TPI) for oil water separation of the effluent treatment plant. This section includes broad project data and the detailed specification may be referred in the document PY 51544 attached herewith.

- PROJECT DATA

| Project | : | BTG Package for 1 X 120MW Gas Based Captive Power Plant |
| --- | --- | --- |
| Customer | : | Tata Steel Limited, Kalinganagar |
| Project Location | : | Kalinganagar, Orissa |
| Plant Capacity | : | 5 m3/hr |

- DESIGN PARAMETERS

- Inlet Effluent Quality

| Sl. No. | Parameter | Unit | Range |
| --- | --- | --- | --- |
|  | pH | - | 6.5 - 8 |
|  | Oil and Grease | ppm | 150 |
|  | Total Suspended Solids | ppm | 200 |
|  | Viscosity of effluent | cp | 1 |
|  | Temperature of effluent | ° C | Ambient |
|  | Specific gravity | - | 0.9 |

- Guaranteed Treated Effluent Quality:

| Sl. No. | Parameter | Unit | Value |
| --- | --- | --- | --- |
| 1 | Oil and Grease | ppm | < 10 |
| 2 | Total Suspended Solids | ppm | 100 |

- Design Data

| Sl. No. | Description | Unit |  |
| --- | --- | --- | --- |
|  | Flow | m3/hr | 5 |
|  | Number of tanks | No. | 1 |
|  | Type of flow |  | Counter current |
|  | Material of construction |  |  |
|  | - Tank (rectangular type) |  | MS-Epoxy Painted |
|  | - Plates |  | FRP with Isopthalic lining |
|  | - Oil skimmer and flow baffle |  | MS-Epoxy Painted |
|  | - Nozzles |  | MS-Epoxy Painted |
|  | Type of plates (profile) |  | Corrugated |
|  | Duty |  | Intermittent |
|  | Location |  | Outdoor |
|  | Operating pressure |  | Atmospheric |

- P&ID

A typical P&ID of the system is enclosed. In case bidder is not able to offer in line with the P&ID, the same is to be discussed and settled during pre-bid stage only.

- CHECK LIST

Bidder to note that Check List shall be completely filled and the data required in-line with Check List shall be submitted along with their Offer to enable Purchaser to evaluate the offer submitted.

| S.No. | Description | Enclosed or [Yes/No] | Remarks/ Comments by Bidder |
| --- | --- | --- | --- |
| 1 | Bidder to confirm compliance with spec. PY-AS-4-M111-1039-01 and its annexure without any deviations. |  |  |
| 2 | Bidder has already raised pre-bid queries (if any) on Purchase specification. |  |  |
| 3 | Bidder Shall submit completely filled following Annexures enclosed with Technical Purchase Specification PY 51563 along with their offer Annexure-I: Key Information Annexure-II: List of Recommended Spare Parts Annexure-III: Special Tools and Tackles Annexure-IV: List of Commissioning spares Annexure-V: Deviation from specification |  |  |
| 4 | Tentative Electrical Load List is enclosed with offer. |  |  |
| 5 | Bidder shall furnish the list of Erection and commissioning spares along with their offer. |  |  |
| 6 | Bidder to fill Deviation list (Refer Annexure-V of PY 51563). Only those deviation indicated in this list will be considered during technical evaluation of offer. Bidder to indicate the deviations which are impractical. |  |  |
| 7 | All other requirements except the deviations brought out under deviation list, have been taken into consideration in the offer. |  |  |
| 8 | Bidder has submitted unpriced “Price bid format” with “Quoted” mentioned against price for each line item of Price Bid Format |  |  |

Note:

Bidder to note that as per BHEL purchase policy, bidders are not allowed to furnish any positive price implications, after the Technical bid opening, except when BHEL changes any technical requirements. Hence, bidders are strictly advised to settle any clarification or deviation during Pre-bid stage by clearly highlighting the queries.

PRICE SCHEDULE

| SL. NO. | DESCRIPTION | QTY. | UNIT PRICE (Rs) | TOTAL PRICE (Rs) |  |
| --- | --- | --- | --- | --- | --- |
| 1.0 | DESIGN, ENGINEERING, MANUFACTURE, SUPPLY, ERECTION SUPERVISION & COMMISSIONING |  |  |  |  |
| 1.1 | Tilted Plate Interceptor assembly | 1 set |  |  |  |
| 1.2 | Erection supervision and commissioning including performance guarantee of the plant as per the specification. |  |  |  |  |
| 1.2.1 | Per Diem rates per Service Engineer including Boarding, Lodging & Local Travel for the erection supervision and commissioning of the set. | 2 days |  |  |  |
| 1.2.2 | Travel expenses from vendor works to project site and back for Service Engineer/Technician (this shall include charges if any for travel time) for the Scope of Service defined in Technical Specification and all its annexure. | 1 |  |  |  |
|  | TOTAL (for Sl. No. 1.0) |  |  |  |
| 2.0 | Recommended Spares (optional price) |  |  |  |  |
| 2.1 | 2 years recommended spares along with their quantities and unit rate for normal trouble free operation of the system described in Sl. No. 1.1 above based on bidders’ experience. Note: List for recommended spares and it’s unit rate to be furnished by bidder. | RO |  |  |  |

NOTES:-

  - Bidder to quote strictly as per BHEL’s NIT requirements.

  - Bidder to note that this is a LUMP SUM Turn-Key Order. Any additional claim after placement of order will not be entertained under any circumstances.

  - Evaluation of L1 bidder shall be based on TOTAL PRICE (Rs.) (Sl. No.1) mentioned above.

  - Bidder to quote the base rates only. All Applicable taxes and duties shall be indicated separately for the Supply Portion and Erection supervision & Commissioning Portion.

  - Bidder shall also submit unpriced copy of the Price-Bid Format with “Quoted” against each line item of the format along with the technical offer.

  - Bidder to quote strictly in the price bid format with line wise itemized price and quantity, failing which the bidder’s offer shall be liable for rejection.

  - For the purpose of tender evaluation, a total of 2 man-days for 1 visit is being considered. However, either or both of the number of man days or no of visits may change on either side based on the actual site requirement.

  - Bidder to quote separately, in an identical format, 2 years operational spares compulsorily (for Bidder’s supply items) item wise with recommended quantity and unit rate. However ordering of the same shall be at the sole discretion of BHEL. If required, Bidder will be informed if the same is also considered for evaluation, before the price bid opening.

Signature of Bidder’s

Authorized representative ......................................

Date.............

TENDER DRAWINGS/DOCUMENTS

| Sl. No. | Description | Drg. / Doc. No. | Rev. No. |
| --- | --- | --- | --- |
| 1 | Technical Purchase Specification for Tilted Plate Interceptor | PY-51563 | 00 |
| 2. | P&ID of Oily Water Separator System | PID-23-02-13-01-291-071 | 00 |
| 3. | QAP Guidelines & Format |  | 00 |
| 4. | Corporate Packing Standard | AA0490010 | 02 |
| 5. | Safety Standard on Structural Ladders | SS/Engg-21 | 00 |
| 6. | General Specification for Painting | GSP-01-00-00-14-000-001 | 02 |

NOTE: The bidder to comply with all the above specifications without any deviation.

| RECORD OF REVISIONS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Rev. No. | Date | Revision Details | Revised By | Approved By |
| 00 | 17.05.19 | First Issue | CHP | MSSN |