| COPYRIGHT AND CONFIDENTIAL The information on this document is the property of BHARAT HEAVY ELECTRICALS LIMITED, It must not be used directly or indirectly in any way detrimental to the interest of the company. | TECHNICAL PURCHASE SPECIFICATION FOR TILTED PLATE INTERCEPTOR |
| --- | --- |

###### INTENT OF SPECIFICATION:

The intent of the specification is to cover the details of scope of design, supply and services of supervision of erection and commissioning for Tilted Plate Interceptor - TPI (Oil Water Separator).

###### GENERAL DESCRIPTION:

  - Design of the Tilted Plate Interceptor shall conform to latest applicable standards.

  - Supplies shall be rendered in conformity with proven design principles. The requirements specified in this document must be fulfilled in its entirety and with maximum reliability. All the components shall be so designed that repairs and overhauling is minimum and can be carried out easily in the shortest possible time.

  - All equipment/items supplied shall conform to the provisions of statutory & other regulations in force in India and the State/Province where the project is being executed.

  - The oily waste water treatment system consists of the following sub-systems:

- Oily water collection

- Pumping system

- Tilted plate interceptor

- Treated water collection

- Oil collection

- Sludge collection

  - Treatment process

The oily waste water is collected from the Boiler and Steam Turbine area in separate collection pits. The collected effluent is then pumped to the TPI for oil and water separation process. Bidder shall design a complete, fully functional TPI for proper & easy operation meeting the performance requirements mentioned in Job specification.

###### SCOPE OF SUPPLY AND SERVICES:

The scope of supply and services covered under this specification shall include design, manufacture, testing, supply, supervision of erection and commissioning of the Tilted Plate Interceptor.

- Tilted plate interceptor tank (mild steel epoxy coated) with internals like plate pack with support, weir plate, flow baffle with support.

- Slotted pipe oil skimmer (Manually adjustable).

- Various flanged nozzles required for the TPI.

- Ladders, platform, hand railing etc. required for the TPI access.

- Foundation bolts for the fixing of TPI.

- Supervision of erection and commissioning.

- Civil input for design of foundation

  - Tilted Plate Interceptor

The tilted plate interceptor shall be used to separate the oil from the oily effluent fed to the TPI. The oily effluent of the Steam Turbine Generator floor wash and Steam Generator area shall be fed to the TPI through separate pumps connected through a common header from respective areas.

The TPI design shall be a single rectangular tank unit of counter current flow type with the corrugated plate pack. The plate pack shall be installed in an inclination. There shall be only one operational bay, no standby bay is required. The effective surface area provided shall be more than the required surface area and the same shall be adequate to meet the treated water parameters as per the specification. The oil skimmer operation shall be manual.

The TPI shall consist of the following components:

- A slotted baffle located at the inlet of the TPI for evenly distributing the incoming oily effluent water towards the separator.

- The plate pack consisting of various corrugated plates on top of each other which shall provide an enlarged separating surface in a TPI separator. This shall enable the oil droplets to coalesce into large droplets. The oil and solids separation shall be through gravity in the counter current flow.

- Slotted pipe oil skimmer to remove the layer of floating oil. The skimmer pipe shall have a lever to rotate the pipe in order to collect the oil layer formed at the surface of the water.

- Weir arrangement for the discharge of treated water (free of oil).

- Nozzles with flanged connection for effluent inlet, treated oil removal, treated water and sludge outlet.

- Accessories such as ladder, platform and hand railing for access of the TPI.

- Foundation bolts and shim plates (as required) for fixing the TPI on the civil foundation.

Note: The civil works for the foundation of the TPI are in the scope of BHEL. However, Bidder shall provide all necessary inputs for the same.

###### QUALITY & INSPECTION

  - Quality Assurance Program

To ensure that the equipment and services under the Scope of Contract manufactured within the Bidder’s works or at his Sub-Vendor’s premises or at the Owner’s site or at any other place or work are in accordance with the specifications, Bidder shall adopt suitable quality assurance program to control such activities at all points, as necessary. Such program shall be outlined by the Bidder and shall be finally accepted by the Owner / Authorized representative after discussions before the award of Contract. The QA program shall be generally in line with ISO-9002/IS-14001. A quality assurance program of the Bidder shall generally cover the following:

System for shop manufacturing and site erection control including process controls, fabrication and assembly controls.

  - Quality Assurance Documents

The Bidder shall submit required no. of copies of the following Quality Assurance documents

  - Material test reports on components as specified by the specification and approved Quality Plans.

  - The inspection plan with verification, inspection plan check points, verification sketches, if used and method used to verify that the inspection and testing points in the inspection plan were performed satisfactorily.

  - Sketches and drawings used for indicating the method of traceability of the radiographs, if applicable, to the location on the equipment.

  - Non-destructive examination results, reports including radiography interpretation reports.

  - Factory tests results for testing required as per applicable codes and standards referred in the specification and approved Quality Plans.

  - Inspection reports duly signed by QA personnel of the customer and Bidder for the agreed customer hold points.

The equipment shall be guaranteed to meet performance requirements required by this specification and rectification shall be carried out until satisfactory results are obtained. The Owner reserves the right to reject the equipment should the performance values fall short of those indicated in the schedule of Technical data sheets.

  - Quality Plan:

Bidder to furnish Quality Plan to BHEL along with offer in their standard format for general review by BHEL. During Detailed engineering, in addition to various tests indicated in this specification, Quality plan will be reviewed with respect to standard Inspection, standard Engineering practices, applicable standards, code etc. Accordingly, various tests required, stages of inspection and appropriate agencies for Inspection will be intimated.  Bidder to abide by the same.

  - Tests & Inspection:

    - The manufacturer shall conduct all tests required to ensure that the equipment furnished shall conform to the requirements of this specification and in compliance with requirements of applicable codes and standards. The particulars of the proposed tests and the procedures for the tests shall be submitted to the Purchaser/Consultant for approval before conducting the tests.

    - The following Inspection and Testing procedures shall be carried out for the equipment as applicable. The detailed procedure shall indicate or specify, without limitation, the following:

          - Visual Inspection.

          - Dimension Checking

          - Dynamic balancing for all rotating parts (if applicable)

          - Hydrostatic / Leak testing for all pressure parts, Pneumatic Leak Test wherever applicable

          - Operation check

          - Liquid penetrant tests or magnetic particle tests for all machined surfaces of pressure parts.

    - As a guide to the bidder, BHEL and end customer M/s TSL reserves the right to witness testing of the item:

  - Any Other Tests not specifically listed but required to ensure the intended performance of the equipment is met.

  - Site Performance Test:

  - Inspection agency:

BHEL/Third Party appointed by BHEL/Customer

The various inspection stages will be witnessed by individual agencies (or) Group of Agencies as per above, in line with approved quality plan.

###### PROTECTION FOR SHOP FABRICATED ITEMS:

# All coated surfaces shall be protected against abrasion, impact, discoloration and any other damages. All exposed threaded portions shall be suitably protected with either a metallic or non-metallic protecting device. The parts which are likely to get rusted due to exposure to weather, should also be properly treated and protected in a suitable manner. All exposed metallic surfaces subject to corrosion shall be protected by shop application of suitable coatings. All surfaces which will not be easily accessible after the shop assembly, shall beforehand be treated and protected for the life of the equipment. All surfaces shall be thoroughly cleaned of all mill scale, oxide and other coatings and prepared in the shop.

# The surfaces that are to be finish-painted after installation or require corrosion protection until installation, shall be shop painted with at least two coats of primer. The finished colors shall be as per manufacturer's standards.

# All material shall be delivered in a clean and usable condition. Openings shall be securely covered against entry of foreign material where appropriate.

###### PACKING AND TRANSPORTATION:

All equipment shall be suitably protected, coated, covered or boxed and crated to prevent damage or deterioration during transit, handling and storage at site till the time of erection. Bidder shall follow necessary road safety rules and shall obtain permission from highway authorities for goods movement.  However, these aspects shall be taken into consideration in the design of the packing for the system.

###### NAME PLATES & TAG PLATES:

# Components whose identity is important for operation and maintenance of the plant shall be provided with permanently attached tag bearing the Purchaser’s coding together with relevant text clearly inscribed.

# A corrosion-resistant nameplate shall be attached to the unit in a clearly visible, easily accessible location. The nameplate shall be stamped with the following information:

# Manufacturer’s name

# Manufacturer’s model number

# Manufacturer’s serial number

# Purchaser’s equipment tag number (item No.)

# Service name

# Weight (kg)

# Hydrostatic test pressure, Bar. (g)

# Other design information of the flow media like flow rate, temperature, pressure etc.

# Nameplates shall be 3 mm (0.12”) thick engraved plate of sufficient rigidity with lettering of a minimum height of 4 mm (0.16”). The method of implementation and labelling will be informed for all components after award of contract.

# Identification tag shall be provided and placed on Bidder furnished item. Tag shall be corrosion resistance, having a larger than diameter of 3 cm, and shall have black identification figures stamped thereon. Figure height shall be larger than 0.5 cm. Tag shall bear the component system designation symbol shown on the Bidder’s drawings.

###### VENDOR DOCUMENTATION:

  - The O&M manuals shall contain the following details as minimum in addition to those indicated in the above table:-

- Identification details of the equipment like BHEL PO NO., Vendor’s Sl. No., Vendors contact address with tel., fax details.

- Description of the equipment.

- Final Data sheets and Drawings of the equipment as per the list mentioned in this specification.

- Recommended two years operational spares.

- Test reports.

  - The erection documentation shall consist of

- All drawings/documents,

- All such drawings/documents, not submitted for review, but essential for erection/ commissioning, e.g. assembly drawings, etc.

- Master document list

- Site dispatchable B.O.M. (if applicable)

  - Vendor shall submit all drawings / documents as per the Document List given below:

| Sl. No. | DRG/DOC. NAME | Date of Submission |
| --- | --- | --- |
| MECHANICAL |  |  |
| M.01 | GA of Tilted Plate Interceptor | 1 week from PO |
| M.02 | Data sheet of Tilted Plate Interceptor | 1 week from PO |
| CIVIL |  |  |
| C.01 | Civil input drawings for the TPI | 1 week from PO |
| MISCELLANEOUS |  |  |
| MIS.01 | Commissioning spares | 2 weeks from PO |
| MIS.02 | Recommended spares | 2 weeks from PO |
| MIS.04 | O&M manual | 6 weeks from PO |
| MIS.05 | Performance Test Procedure | 6 weeks from PO |

Note: The date of first submission is indicated above. Bidder shall submit all subsequent revision within 7 working days of comments.

###### GUARANTEES

The guarantees shall form contract guarantees to be demonstrated through an approved performance test after the completion of the Plant. The schedule shall be finalized during the detail engineering stage.

###### DOCUMENTS TO BE SUBMITTED ALONG WITH THE OFFER

- Guaranteed outlet quality (sludge qty)

- Filled in Annexures-I, II, III, IV & V of PY-51563

- Un-priced Price bid format as given in Job specification.

ANNEXURE – I

KEY INFORMATION

|  | Name of the Bidding Company |  |  |
| --- | --- | --- | --- |
|  | Registered in (mention the name of the Country) |  |  |
|  | Name, designation, telex & telephone number and postal address of responsible officer of Bidder to whom all reference shall be made for expeditious co-ordination. |  |  |
|  | Name, designation, telex & telephone number and postal address of responsible officer of Indian Agent. |  |  |
|  | Bidder’s proposal number |  |  |
|  | Bidder’s proposal date |  |  |
|  | Validity of offer, counted from the date of opening of bid |  |  |
|  | Guaranteed completion period, counted from date of issuance of LOI/TOI |  |  |
|  | Confirm that Scope of supply and services are exactly as per specification requirement |  | Yes/No |
|  | Confirm Technical Compliance with Specification |  | Yes/No |
|  | Confirm that Guarantees are as per Job Specification |  | Yes/No |
|  | Confirm that List of Recommended Spares has been furnished as per Annexure-II |  | Yes/No |
|  | Confirm that List of Special Tools & Tackles has been furnished as per Annexure-III |  | Yes/No |
|  | Confirm that deviations, if applicable, have been furnished as per Annexure-V |  | Yes/No |

Signature of Bidder’s

Authorized representative ......................................

Date.............

ANNEXURE – II

LIST OF RECOMMENDED SPARE PARTS

(Optional prices only have to be quoted)

Bidder shall tabulate in the proforma below list of all spare parts as recommended by the respective manufacturer for regular, reliable operation for a period of 2 years. In case the Bidder has to add any other relevant information, the same shall be indicated herein. Continuation sheets of like size and format may be used as per Bidder’s requirements.

Sl.       Description     Quantity   	Unit               Total           Delivery     	 	Remarks                No                                                      Price              Price           Period

Signature of Bidder’s

Authorized representative ......................................

Date.............

ANNEXURE – III

LIST OF SPECIAL TOOLS AND TACKLES

Bidder shall tabulate in the proforma below list of all tools and tackles as recommended by the respective manufacturer for regular, reliable operation. In case the Bidder has to add any other relevant information, the same shall be indicated herein. Continuation sheets of like size and format may be used as per Bidder’s requirements.

| Sl.No. | Description | Quantity | Remarks |
| --- | --- | --- | --- |
| a |  |  |  |
| b |  |  |  |
| c |  |  |  |
| d |  |  |  |

Signature of Bidder’s

Authorized representative ......................................

Date.............

ANNEXURE – IV

LIST OF COMMISSIONING SPARES

Bidder shall tabulate in the proforma below list of all spare parts as recommended by the respective manufacturer for regular, reliable operation. In case the Bidder has to add any other relevant information, the same shall be indicated herein. Continuation sheets of like size and format may be used as per Bidder’s requirements.

| Sl.No. | Description | Quantity | Unit price | Total Price | Delivery Period | Remarks |
| --- | --- | --- | --- | --- | --- | --- |

ANNEXURE – V

DEVIATION FROM SPECIFICATION

If the proposal submitted has got any deviation from the technical stipulations in the bidding document, the Bidder shall tabulate below the full particulars of such deviations and shall sign below. Additional sheets may be enclosed, if necessary. Deviation is to be furnished with mention of specific clause numbers. Technical and commercial deviations to scope of supply and services, shall be indicated separately. Bidders shall bring out only those deviations which are impractical to meet (or) not advisable

| Sl.No. | CLAUSE NO. | DESCRIPTION AS PER SPECIFICATION | DEVIATION BY BIDDER |
| --- | --- | --- | --- |

We confirm that all the deviations/exceptions to the Technical Specification PY51563, Job

Specification and enclosures including reference documents attached, are listed in this Annexure

only. No other deviations or exceptions even if mentioned elsewhere shall be considered for any

technical/ commercial evaluation or for ordering.

Signature of Bidder’s

Authorized representative.......................................

Date .............

VARIANT TABLE

| Var. No. | Item | STP Capacity | Material Code | Ref. Drg./ Doc. |
| --- | --- | --- | --- | --- |
| 00 | TILTED PLATE INTERCEPTOR | 5m3/hr | PY9751563003 | TATA 120 MW |

| RECORD OF REVISIONS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Rev. No. | Date | Revision Details | Revised By | Approved By |
| 00 | 13.05.19 | First Issue | ------- | MSSN |